## READ FIRST (old - w scale text) (hidden)
Climate-ready Housing Design Guide V1
BACKGROUND
BC Housing is developing a Climate-ready Housing Design Guide ('the Guide') for BC Building Code Part 3 residential buildings (e.g. multifamily residential buildings) to promote housing that is resilient in the face of climate change. The Guide focuses on climate adaptation (e.g. preparing for climate change impacts) but draws strong linkages with best practices for mitigating climate change through lower-carbon design. Building off the Climate Resilience Guidelines for BC Health Facility Planning and Design (released in December 2020), the Province of BC Guidebook & Standards for Climate Resilient Public Sector Buildings (in progress as of July 2022) and other leading frameworks, BC Housing and Integral Group have compiled a draft set of objectives, recommended approaches, technical standards and recommended resilient design strategies to form the basis of the Climate-ready Housing Design Guide.
In February 2021, these draft materials were reviewed with a Task Force of subject matter experts to:
- Refine language so that requirements are clear, practical and feasible for design teams
- Identify gaps so that requirements adequately address the select set of climate hazards
- Identify those requirements that may be better-suited as recommended resilient design strategies
- Confirm requirements with strong low carbon resilience potential
These draft materials have undergone subsequent revision and are now being distributed to the industry for broader review as Climate-ready Housing Design Guide v0.1
PROJECT BOUNDARIES & ADDITIONAL CONTEXT
The Guide is intended to cover a range of BC Building Code Part 3 residential building typologies and tenures (e.g. high-rise, low-rise, townhouses, market rate and affordable), but not single-family homes. The Guide is designed with new construction in mind, but may be expanded to cover retrofits and renovations of existing buildings in the future. The Climate-ready Housing Design Guide is intended to be a living document that is continuously updated as new information and best practices become available. The focus of this version of the Guide has been on the following three key categories: - General Resilience
- Warmer Temperatures & Extreme Heat
- Wildfires & Air Quality Impacts
Draft materials for the following hazards/categories are provided for reference and to show that they are being considered, but these have not yet been fully developed:
- Flooding
- Seismic Events & Slope Hazards
- Power Outage
- Wind & Storms
- Snowfall
- Chronic Stressors (Water Shortage & Drought, Moisture & Humidity, Freeze/Thaw)
- Social Dimensions
LOW CARBON RESILIENCE RATINGS
While the approaches, standards and strategies profiled in this Guide are focused on building housing resilience to climate impacts (climate adaptation), the degree to which each approach may also help reduce operational and embodied greenhouse gas (GHG) emissions from the development (climate mitigation) has also been considered. Wherever possible, users of this Guide are encouraged to prioritize resilience strategies that also reduce GHG emissions. This 'low carbon resilience' approach helps to achieve multiple goals, including GHG emissions goals set at the community, provincial and national scale, while also leveraging a host of other co-benefits such as more comfortable and enjoyable spaces, energy cost savings, and ecological restoration.
The following scale has been used to evaluate the Low Carbon Resilience Potential of each climate resilience approach:
- High: Very likely to contributes to GHG emissions reductions/this would be a mitigation strategy recommended even if there were no adaptation benefit
- Moderate: likely contributes to some GHG emissions reductions
- Neutral: likely to have little impact on increasing or decreasing GHG emissions
- Low: negligible impact on GHG emissions (neither positive or negative)
- Negative: likely contributes to increased GHG emissions
Information has also been provided on the degree to which Resilient Design Strategies in this Guide support other co-benefits such as seismic resilience and pandemic response. Further detail on the impact each approach may have on GHG reduction and other co-benefits is also described in the Approaches & Standards and Resilient Design Strategies sheets in this Guide.
ADDITIONAL BACKGROUND RESOURCES
Provided below is a list of additional climate change resilience design consideration resources that are supplementary to those provided in the "Approaches & Standards" sheet:
• BC Housing Design Guidelines and Construction Standards (BCH, 2019)
• Guidebook & Standards for Climate Resilient Public Sector Buildings (Province of BC, in draft 2022)
• Climate Change Considerations for Building Enclosure Engineers Practice Advisory (EGBC, 2022)
• Enhancing the Liveability and Resilience of Multi-Unit Residential Buildings (MURBs) MURB Design Guide Version 2.0 (Kesik et al., 2019)
• Climate Resilience Guidelines for BC Health Facility Planning & Design (BC Health Authorities, 2020)
• Voluntary Resilience Standards: An Assessment of the Emerging Market for Resilience in the Built Environment (Energy, Kresge and Barr Foundations, 2017)
• UK Housing: Fit for the Future? (UK Committee on Climate Change, 2019)
• RELi 2.0 Rating Guidelines for Resilient Design + Construction (USGBC, 2018)
• Resilient Buildings: Informing Maintenance for Long-term Sustainability Final Industry Report, Project 1.53 (Australia Sustainable Built Environment National Research Centre, 2018)
• Climate Resiliency Guidance (Boston Planning & Development Agency, 2017)
• Ready to Respond: Strategies for Multifamily Building Resilience (Enterprise Green Communities, 2015)
• Resilience Planning New Construction: Checklist - Toronto Green Standards Version 3.0 (City of Toronto, 2018)
USE DISCLAIMER
This Guide is provided for general information. The greatest care has been taken to confirm the accuracy of the information contained herein. However, the authors, funders, publisher, and other contributors assume no liability for any damage, injury, loss, or expense that may be incurred or suffered as a result of the use of this publication, including products, building techniques, or practices. The views expressed herein do not necessarily represent those of any individual contributor or BC Housing. Seek specific information on the use of products, the requirements of good design and construction practices and requirements of the applicable building codes before undertaking a construction project. Consult the manufacturer’s instructions for construction products, and also speak with and retain consultants with appropriate engineering or architectural qualifications, and appropriate municipal and other authorities, regarding issues of design and construction practices. Detailed provisions of the building code (British Columbia Building Code) have not been specifically referenced, and use of the Guide does not guarantee compliance with code requirements. Always review and comply with the specific requirements of the applicable building codes for each construction project.
© BC Housing 2022
ACKNOWLEDGEMENTS
This Guide has been developed by the BC Housing Mobilizing Building Adaptation and Resilience (MBAR) Team, with leadership by Wilma Leung, Magdalena Szpala, Remi Charron, Karen Williams, and Jessica Woolliams.
Technical work was led by Integral Group Consulting with valuable input from a Task Force of industry experts from the following organizations:
• Integral Group: Lisa Westerhoff, Craig Dedels, Robin Hawker, Anika Bell, Chris Doel, Thomas Bamber, Gordon McDonald, Louise Hemott
• Ausenco: John Sherstobitoff
• Kerr Wood Leidal: Mike Currie
• RDH: Robert LePage
• Horizon Engineering: Karen Savage
• Focal Engineering: Susan MacDougall, Danny Taylor
• Technical Safety BC: Ainaz Bozorgzadeh
• Natural Resources Canada: Erin Greco
• BC Non-Profit Housing Association: Ian Cullis, Jackie Kanyuk
• University of BC: Ralph Wells
• TD Systems: Peter Osuchowski
• City of Vancouver: Charling Li
• Urban Development Institute: Jeffery Fischer

## READ FIRST
Climate-ready Housing Design Guide V1
BACKGROUND
BC Housing is developing a Climate-ready Housing Design Guide ('the Guide') for BC Building Code Part 3 residential buildings (e.g. multifamily residential buildings) to promote housing that is resilient in the face of climate change. The Guide focuses on climate adaptation (e.g. preparing for climate change impacts) but draws strong linkages with best practices for mitigating climate change through lower-carbon design. Building off the Climate Resilience Guidelines for BC Health Facility Planning and Design (released in December 2020), the Province of BC Guidebook & Standards for Climate Resilient Public Sector Buildings (in progress as of July 2022) and other leading frameworks, BC Housing and Integral Group have compiled a draft set of objectives, recommended approaches, technical standards and recommended resilient design strategies to form the basis of the Climate-ready Housing Design Guide.
In February 2021, these draft materials were reviewed with a Task Force of subject matter experts to:
- Refine language so that requirements are clear, practical and feasible for design teams
- Identify gaps so that requirements adequately address the select set of climate hazards
- Identify those requirements that may be better-suited as recommended resilient design strategies
- Confirm requirements with strong low carbon resilience potential
These draft materials have undergone subsequent revision and are now being distributed to the industry for broader review as Climate-ready Housing Design Guide v0.1
PROJECT BOUNDARIES & ADDITIONAL CONTEXT
The Guide is intended to cover a range of BC Building Code Part 3 residential building typologies and tenures (e.g. high-rise, low-rise, townhouses, market rate and affordable), but not single-family homes. The Guide is designed with new construction in mind, but may be expanded to cover retrofits and renovations of existing buildings in the future. The Climate-ready Housing Design Guide is intended to be a living document that is continuously updated as new information and best practices become available. The focus of this version of the Guide has been on the following three key categories: - General Resilience
- Warmer Temperatures & Extreme Heat
- Wildfires & Air Quality Impacts
Draft materials for the following hazards/categories are provided for reference and to show that they are being considered, but these have not yet been fully developed:
- Flooding
- Seismic Events & Slope Hazards
- Power Outage
- Wind & Storms
- Snowfall
- Chronic Stressors (Water Shortage & Drought, Moisture & Humidity, Freeze/Thaw)
- Social Dimensions
LOW CARBON RESILIENCE RATINGS
While the approaches, standards and strategies profiled in this Guide are focused on building housing resilience to climate impacts (climate adaptation), the degree to which each approach may also help reduce operational and embodied greenhouse gas (GHG) emissions from the development (climate mitigation) has also been considered. Wherever possible, users of this Guide are encouraged to prioritize resilience strategies that also reduce GHG emissions. This 'low carbon resilience' approach helps to achieve multiple goals, including GHG emissions goals set at the community, provincial and national scale, while also leveraging a host of other co-benefits such as more comfortable and enjoyable spaces, energy cost savings, and ecological restoration.
Information has also been provided on the degree to which Resilient Design Strategies in this Guide support other co-benefits such as seismic resilience and pandemic response. Further detail on the impact each approach may have on GHG reduction and other co-benefits is also described in the Approaches & Standards and Resilient Design Strategies sheets in this Guide.
USE DISCLAIMER
This Guide is provided for general information. The greatest care has been taken to confirm the accuracy of the information contained herein. However, the authors, funders, publisher, and other contributors assume no liability for any damage, injury, loss, or expense that may be incurred or suffered as a result of the use of this publication, including products, building techniques, or practices. The views expressed herein do not necessarily represent those of any individual contributor or BC Housing. Seek specific information on the use of products, the requirements of good design and construction practices and requirements of the applicable building codes before undertaking a construction project. Consult the manufacturer’s instructions for construction products, and also speak with and retain consultants with appropriate engineering or architectural qualifications, and appropriate municipal and other authorities, regarding issues of design and construction practices. Detailed provisions of the building code (British Columbia Building Code) have not been specifically referenced, and use of the Guide does not guarantee compliance with code requirements. Always review and comply with the specific requirements of the applicable building codes for each construction project.
© BC Housing 2022
ADDITIONAL BACKGROUND RESOURCES
Provided below is a list of additional climate change resilience design consideration resources that are supplementary to those provided in the "Approaches & Standards" sheet:
• BC Housing Design Guidelines and Construction Standards (BCH, 2019)
• Guidebook & Standards for Climate Resilient Public Sector Buildings (Province of BC, in draft 2022)
• Climate Change Considerations for Building Enclosure Engineers Practice Advisory (EGBC, 2022)
• Enhancing the Liveability and Resilience of Multi-Unit Residential Buildings (MURBs) MURB Design Guide Version 2.0 (Kesik et al., 2019)
• Climate Resilience Guidelines for BC Health Facility Planning & Design (BC Health Authorities, 2020)
• Voluntary Resilience Standards: An Assessment of the Emerging Market for Resilience in the Built Environment (Energy, Kresge and Barr Foundations, 2017)
• UK Housing: Fit for the Future? (UK Committee on Climate Change, 2019)
• RELi 2.0 Rating Guidelines for Resilient Design + Construction (USGBC, 2018)
• Resilient Buildings: Informing Maintenance for Long-term Sustainability Final Industry Report, Project 1.53 (Australia Sustainable Built Environment National Research Centre, 2018)
• Climate Resiliency Guidance (Boston Planning & Development Agency, 2017)
• Ready to Respond: Strategies for Multifamily Building Resilience (Enterprise Green Communities, 2015)
• Resilience Planning New Construction: Checklist - Toronto Green Standards Version 3.0 (City of Toronto, 2018)
ACKNOWLEDGEMENTS
This Guide has been developed by the BC Housing Mobilizing Building Adaptation and Resilience (MBAR) Team, with leadership by Wilma Leung, Magdalena Szpala, Remi Charron, Karen Williams, and Jessica Woolliams.
Technical work was led by Integral Group Consulting with valuable input from a Task Force of industry experts from the following organizations:
• Integral Group: Lisa Westerhoff, Craig Dedels, Robin Hawker, Anika Bell, Chris Doel, Thomas Bamber, Gordon McDonald, Louise Hemott
• Ausenco: John Sherstobitoff
• Kerr Wood Leidal: Mike Currie
• RDH: Robert LePage
• Horizon Engineering: Karen Savage
• Focal Engineering: Susan MacDougall, Danny Taylor
• Technical Safety BC: Ainaz Bozorgzadeh
• Natural Resources Canada: Erin Greco
• BC Non-Profit Housing Association: Ian Cullis, Jackie Kanyuk
• University of BC: Ralph Wells
• TD Systems: Peter Osuchowski
• City of Vancouver: Charling Li
• Urban Development Institute: Jeffery Fischer

## Approaches & Standards
# | RESILIENCE DESIGN APPROACH | TECHNICAL STANDARDS | KEY CONSIDERATIONS (Notes for application based on building type, risk level, etc.) | DISCIPLINE CATEGORY | ADDITIONAL RESOURCES | FUTURE CONSIDERATIONS (Items to be considered for future versions of this Guide) | LOW CARBON RESILIENCE (LCR) POTENTIAL (Negative / Low / Moderate / High) | INTERACTIONS BETWEEN RESILIENCE & GHG EMISSIONS REDUCTIONS | EMBODIED EMISSIONS (Decrease / Neutral / Increase) | OPERATIONAL EMISSIONS (Decrease / Neutral / Increase)
1 | GENERAL RESILIENCE
Guiding Objectives: |  | ◊ Factor climate resilience considerations into all capital expenditures and incorporate life-cycle costs (LCC) of buildings under future climate conditions. Offset resilience investments with projected operational costs savings over building lifespans. ◊ Align climate change adaptation measures with efforts to reduce carbon emissions.
1.1. | Use future climate projections for priority hazards to inform the design and development strategies of the buildings (including orientation, exposure, and materials selection), critical building systems, and their associated components, through to anticipated end of useful building life. | Use future climate projections looking at least 30 and/or 50 years into the future (depending on the lifespan of building components) using a high emissions scenario (e.g. Representative Concentration Pathway 8.5 (RCP8.5)), based on data provided by climate science authorities (e.g., Pacific Climate Impacts Consortium (PCIC) online data portal). In absence of available future climate data, design heating, ventilation, and air conditioning (HVAC) systems based on design summer conditions that are 3°C higher (both dry bulb and wet bulb) than the temperatures recommended by ASHRAE or the BC Building Code. Provide a high performing building envelope that uses passive design and is informed by hazard exposure analysis and future climate projections to 30-years from construction. Provide a narrative within the design reports confirming use of future climate projections. | Building Type: all residential building types. | General Resilience | For additional resources on climate projections in BC, refer to: • Pacific Climate Impacts Consortium Design Value Explorer (PCIC, 2022) • Pacific Climate Impacts Consortium Climate Explorer (PCIC, 2022) • ClimateData.ca For additional guidance on durability of buildings, refer to: • CAS S478 (Guideline on Durability in Buildings) | • This Guide is currently designed for new construction. Consider exploring adjustments to this Guide to include major renovations and renewals of existing buildings. • A cost-benefit reference resource for each of the technical standards would benefit this Guide. • The National Research Council is working on producing future climate projections for weather extremes. This may be an additional resource for future climate projections, when available. This resource may be particularly valuable for considering future winter cold temperature extremes. • Highlight the resilience measures that are inside private units vs. those that are in common areas and are easier to access. • Provide a column on maintenance and operations considerations for all standards in this document. • Within the "Resilient Design Strategies" sheet, add a column specifying who is responsible (e.g., architect, building manager, etc.) and when the strategy should be implemented. | Moderate | - Designing properly for future climates may reduce retrofit requirements and therefore reduce embodied carbon over the lifespan of the building | Decrease | Neutral
1.2. | Explore opportunities for modular solutions to improve flexibility and responsiveness over time. | Use modular design for cooling, air handling, and/or electrical systems as a way to limit oversizing. However, all distribution networks (including but not limited to ductwork and piping) should be designed and constructed for 30-year future climate conditions from opening day. | Building Type: all residential building types. | General Resilience |  |  | Moderate | Energy Efficiency & Emissions Reductions: - Designing appropriately sized equipment for future climates may decrease the need for retrofits due to undersized equipment. | Decrease | Decrease
1.3. | Prioritize climate resilience strategies that have low operational or embodied greenhouse gas emissions. | Identify design strategies that reduce operational and embodied emissions. Emphasize low carbon resilience (LCR) through strategies that simultaneously reduce emissions and enhance resilience. In particular, aim to prioritize measures to minimize usage of refrigerants with high global warming potential and prevent leakage. | Building Type: all residential building types. | General Resilience | Further detail on strategies provided in the Warmer Temperatures & Extreme Heat section of this Guide. |  | High |  | Decrease | Decrease
1.4. | Dedicate a section in the Design and Construction Package to climate risks and resilience. | This section should (i) list the buildings, critical building systems (e.g. electricity, plumbing, ventilation, heating), and how they take into account the variability, extremes, frequency, duration, and unpredictability of weather events associated with a changing climate to building end life; and, (ii) describe the following: • Changes in temperature, precipitation and other climate variables identified as relevant in the climate hazard exposure analysis, • Overall climate resilience design objectives and goals, • Adjustments to design criteria, parameters and / or conditions as a result of the changes in climatic variables noted above (additionally, specify these design considerations on the relevant design drawings), • The type and extent of design modifications to account for climate change to building end life, • Climate-related assumptions and risk thresholds that underpin proposed designs, and • Data and information sources used for proposed designs. | Building Type: all residential building types. | General Resilience |  |  | Low |  | Neutral | Neutral
1.5. | Provide an amenity room connected to enhanced backup power and equipment to act as a cooling centre and clean air refuge area for vulnerable residents (e.g., seniors) and as a central location for emergency support and services including in power outages. | In this space or in another location as appropriate, provide: • Accessible washrooms, • Kitchenette with basic supplies, • Access to emergency supplies such as first aid equipment and food and water to last at least 72 hours per person (based on anticipated occupancy), • Solar chargers or battery backup for electronic devices, ideally with wireless internet backup or freely available data, to help residents stay connected during emergencies, • Extra outlets to power medical equipment (e.g. respirators) and charge electric wheelchairs, • A way for residents with medical conditions to keep their medication cold if needed (e.g. refrigerator in the refuge area), • Dedicated HVAC system (including mechanical cooling) capable of accommodating overheating events and maintaining a maximum indoor temperature of 24°C (75.2°F), • Backup power for HVAC system, and • Provision of 100% outdoor air ventilation (with filtration) and appropriate filtration capability for maintaining healthy indoor air conditions during wildfire events 14 days in duration (target MERV 15). • Option for natural ventilation and daylight in case of power outage. Provide a narrative within the mechanical design report and an annotated drawing describing the above. | Building Type: only relevant for multi-unit residential buildings. | General Resilience | For additional resources on indoor temperature management, overheating and ventilation, refer to: • The BC Housing Design Guidelines and Construction Standards (BCH, 2019) • The Minimum Climate Resilience Standards for Public Sector Buildings (BC Ministry of Environment and Climate Change Strategy, in draft) |  | Low |  | Increase | Neutral
1.6. | Develop and implement a Landscaping Plan to that contributes to a regional improvement in resilience (e.g., reduces local urban heat island effect, protects buildings from sun, wind, and rain, improves green space, mitigates flood risk, supports mental health) by employing landscaping measures and nature-based approaches. | The Plan should note potential synergies with nature-based approaches for flood mitigation and summer heat reduction. Landscaping strategies that may be considered include, but are not limited to: • Rain gardens, • Bio-retention ponds, • Stream daylighting, • Engineered wetlands, • Permeable pavement, • Infiltration trenches, • Deciduous trees at south and west building orientations, • Rainwater tree trenches, and/or • Green roofs. Non-invasive, native, drought- and heat-tolerant plantings should be prioritized and smart irrigation strategies (such as drip irrigation and rainwater storage) should be employed. All plant selections should be appropriate for the current and projected micro-climate conditions of the site. For optimal health and climatic co-benefits (e.g. urban heat island effect reduction), selections should enhance natural canopy at the site an incremental rate of 10% per year until 40% coverage is attained. Promote views and connection to nature to improve mental health. On-site detention using non-infiltrating storage devices (e.g., underground detention tanks) can also be considered. All detention systems should be designed by a qualified professional. Provide a landscaping plan and plant list, with narratives and annotated drawings as appropriate. | Building Type: all residential building types. Additional Risk Considerations: All landscaping design should include and prioritize fire safety considerations. Refer to section 3 Wildfires and Air Quality Impacts for further guidance. | Landscape | For additional resources on landscape design measures to improve resilience, refer to: • The BC Housing Design Guidelines and Construction Standards (BCH, 2019) • The Minimum Climate Resilience Standards for Public Sector Buildings (BC Ministry of Environment and Climate Change Strategy, in draft) | • Food gardens and edible landscaping may be explored in future versions of this Guide. • It should be explored whether vegetation can be factored into energy models to illustrate the impact on cooling loads. | Moderate | Energy Efficiency & Emissions Reductions: - Reduce cooling demands/summer heat gains. | Decrease | Decrease
1.7. | Develop a Building Durability and Asset Management Plan consistent with CSA S478 that includes guidance for the following operations in future climate conditions: a) Maintenance b) Renewals c) Operations | Integrate the plan with Building Information Modelling (BIM) processes. Within this document: • Produce a design life table specifying component lifespans to indicate durability and longevity, and • Indicate where components achieve longer than average service lifespans and how climate change conditions have been considered for these components near the end of their lifespans. Refer to 1.1. of this document for recommendations on obtaining future climate conditions. | Building Type: only relevant for multi-unit residential buildings. | Planning |  |  | Low |  | Neutral | Neutral
1.8. | Develop a Construction Contractor Quality Management Plan. | The Plan should demonstrate: • How construction materials will be kept dry throughout the construction process • How products that will be contained within the building envelope will be kept dry before being sealed in place • How dust and contamination of construction will be managed • Plans to stop work during construction due to overheating and air quality concerns | Building Type: all residential building types. | Planning |  |  | Moderate | Materials Management: - Reduce embodied carbon. - Keeping the building materials in good condition may extend their lifetime and reduce the need for retrofits. | Decrease | Neutral
1.9. | Develop an operational Utility Interruption & Site Access Plan. | The Plan should address: • Probable causes and likelihood of utility outage at the building, including power, potable water, sanitary, and stormwater, • Probable causes and likelihood of site access interruption, • Impact of service interruption to the building over the course of 72 hours, • Recommendations and requirements for building operators during service interruption, and • Strategies implemented to reduce risk and impact of utility outage and site access interruption. | Building Type: all residential building types. | Planning | Note that backup power considerations are detailed in the Power Outage section, to be explored in future versions of the Guide. |  | Low |  | Neutral | Neutral
2 | WARMER TEMPERATURES & EXTREME HEAT
Guiding Objectives: |  | ◊ Strive to improve thermal comfort and safeguard the health of occupants into the future. ◊ Prioritize passive design strategies to reduce energy and emissions and improve passive survivability. Where necessary for thermal comfort and occupant health and safety, incorporate active cooling measures. ◊ Emphasize low carbon resilience (LCR) through strategies that simultaneously reduce emissions and enhance resilience (note measures taken to minimize high global warming potential refrigerant usage and prevent leakage).
2.1. | Perform a thermal safety evaluation & energy modelling for all buildings to identify opportunities to minimize active cooling demands through passive strategies. | The evaluation & energy modelling should: • Adhere to the BC Energy Step Code (BC ESC) and the City of Vancouver Energy Modelling Guidelines, • Be performed using current climate data and using future climate projections looking at least 30 years into the future, • Evaluate the effectiveness of different passive cooling and heat gain reduction options, • Model each internal space independently, • Include thermal bridging analysis by an energy professional adherent to the City of Vancouver Energy Modelling Guidelines (2018), or CSA Z5010:21 - Thermal bridging calculation methodology, • Identify and recommend opportunities to effectively incorporate passive cooling measures, • Demonstrate that the building performs at or better than a Cooling Energy Demand Intensity (CEDI) target of between 15kWh/m2/yr and 30kWh/m2/yr (depending on the local climate zone), to promote a cooling approach that incorporates occupant demand reduction, comfort, and climate resilience, and • Demonstrate that the nighttime temperature does not rise above 26⁰C more than 1% of the year, to prevent nighttime heat stress. Note that passively and partially cooled buildings (i.e. buildings without full mechanical cooling in all occupied spaces) should not exceed more than 20 overheating hours per year for any zone. Provide a Energy Modelling and Thermal Safety Report with modelling results with narratives and annotated drawings as appropriate that summarize measures included to minimize cooling demand. | Building Type: all residential building types. Population Type: particularly important for housing for sensitive populations (e.g. seniors housing, family housing, and housing for people with increased care needs) | Modelling | For additional resources on this topic, refer to: • The BC Housing Design Guidelines and Construction Standards (BCH, 2019) • The Minimum Climate Resilience Standards for Public Sector Buildings (BC Ministry of Environment and Climate Change Strategy, in draft) • City of Vancouver 2021 Rezoning Policy (City of Vancouver, 2021) • Pacific Climate Impacts Consortium Design Value Explorer (PCIC, 2022) • Pacific Climate Impacts Consortium Climate Explorer (PCIC, 2022) • ClimateData.ca For over heating temperature thresholds, refer to the Passively Cooled Buildings section of the City of Vancouver Energy Modelling Guidelines (City of Vancouver, 2018) | • Consider life-cycle cost analysis during CEDI target recommendations. • Provide guidance on humidity considerations as well as temperature considerations. • Provide guidance on how to consider the impacts of urban heat island effect and how to incorporate into energy modelling. • Consider providing specific Total Energy Use Intensity (TEUI) targets. • Consider providing specific embodied carbon life-cycle assessment targets. | High | Energy Efficiency & Emissions Reductions: - By planning for extreme heat brought on by future climates in the design phase, the building can avoid additional energy costs from tenants employing individual strategies in the future (e.g. tenants purchasing individual air conditioning units for their suites). - Reduce cooling demands/summer heat gains. - Employing passive cooling strategies also reduces embodied GHG emissions associated with the mechanical systems. - GHG emissions from refrigerant use can be high. | Decrease | Decrease
2.2. | Design robust building envelopes with enhanced thermal performance. | The Peak Thermal Load (PTL) of the building enclosure (wall, roof, floor, glazing) should achieve the highest step of BC Energy Step Code. Excessive cladding attachments or other penetrations that cause thermal bridging should be avoided unless required for design against future wind loading. Operational carbon emission mitigation benefits should be considered and optimized against embodied carbon emissions associated with increased insulation. Provide within the Energy Modelling and Thermal Safety Report annotated drawings and narratives, as appropriate, that summarize measures for enhanced thermal performance while balancing associated embodied carbon. | Building Type: all residential building types. | Envelope & Enclosure | For additional resources on this topic, refer to: • The Minimum Climate Resilience Standards for Public Sector Buildings (BC Ministry of Environment and Climate Change Strategy, in draft) |  | High | Energy Efficiency & Emissions Reductions: - By planning for extreme heat brought on by future climates in the design phase, the building can avoid additional energy costs from tenants employing individual strategies in the future (e.g. tenants purchasing individual air conditioning units for their suites). - Reduce cooling demands/summer heat gains. - Employing passive cooling strategies also reduces embodied GHG emissions associated with the mechanical systems. - GHG emissions from refrigerant use can be high. | Decrease | Decrease
2.3. | Develop an Extreme Heat Management Plan. | The Plan should demonstrate: • How the project has considered future climate projections based on data provided by climate science authorities (e.g. PCIC), • How future weather files have been used to augment energy modelling, • Minimum and maximum temperature ranges for different zones of the building, • Measures in place to design for overheating hours not to exceed acceptable limits over building design life as specified in 2.1, • Compliance with nighttime temperature threshold limits specified in 2.1, • The overall approach to temperature regulation (e.g. active and passive shading), • Considerations for vulnerable people within the occupant demographic (e.g. older adults, people with specific care needs), and • Plans to stop work during construction due to overheating concerns. | Building Type: all residential building types. | Planning |  |  | Negative | - Including increased mechanical cooling in a building may increase both embodied and operational GHG emission. | Increase | Increase
2.4. | Provide means of passive cooling or passive heat gain reduction strategies to reduce demand on cooling equipment. Passive cooling and heat gain reduction strategies are to be prioritized over mechanical cooling. Mechanical cooling should be installed as supplementary in all buildings, if passive strategies are insufficient to maintain year-round thermal safety. | Passive strategies to be considered include (but are not limited to) the following: • Optimizing building location, orientation, shape, and geometry for reduced year-round energy requirements, • Designing buildings with central courtyards and single loaded corridors to enable suite cross- ventilation, • Exterior shading (passive, active and compatible with operable windows), capable of reducing solar gains to 20 watts/m2 through windows on south and west facades between the months of April and October, • Operable windows carefully oriented to promote cross-ventilation, • Reduced window-to-wall ratios, • Enhanced, continuous insulation, • High performance glazing that minimizes incident solar radiation (e.g. low Solar Heat Gain Coefficient coatings), and • Optimized selection of exterior building colours and surface finishes to account for heat gain. • Where windows are single-sided, target cross-ventilation where possible and provide window openings of 4% of floor area to meet CIBSE TM 59 with passive cooling only. For each suite and/or home, include at least two operable windows or door openings to obtain direct outdoor air and provide a source of backup ventilation. For CEDI targets, refer to standard 2.1 in this document. Document recommendations within the Energy Modelling and Thermal Safety Report. | Building Type: all residential building types. | Architecture | For additional resources on this topic, refer to: • The BC Housing Design Guidelines and Construction Standards (BCH, 2019) • The Minimum Climate Resilience Standards for Public Sector Buildings (BC Ministry of Environment and Climate Change Strategy, in draft) • The Climate Change Considerations for Building Enclosure Engineers Practice Advisory (EGBC, 2022) • The Overheating Considerations for Existing Multi-Unit Residential Buildings Practice Advisory (EGBC, in draft, to be published in 2022) | • Provide guidance or resources on life-cycle cost analysis for passive strategies to develop an understanding of the complete cost picture. | High | Energy Efficiency & Emissions Reductions: - Passive cooling strategies may reduce cooling demands/summer heat gains. - Employing passive cooling strategies also reduces embodied GHG emissions associated with the mechanical systems. - GHG emissions from refrigerant use can be high. | Decrease | Decrease
2.5. | Size and design capacity for building HVAC systems (e.g. heat recovery ventilators, heat pumps, etc.) to maintain required thermal safety under future climate conditions, employing modular or mixed mode systems where appropriate. | HVAC systems should: • Be sized to provide thermal safety for the climate on opening day and be prepared to provide thermal safety for the climate 30 years in the future from building construction especially for south and west facing residential apartments, • Be sized based on future weather files sourced from climate science authorities (e.g. PCIC) or, in the absence of this, be designed based on design summer conditions that are 3°C higher (both dry bulb and wet bulb) than the temperatures recommended by ASHRAE or the BC Building Code, • Utilize heat recovery (e.g. heat recovery ventilators (HRV) or energy recovery ventilators (ERV)) and select high efficiency systems with boost and bypass modes, • Use modular equipment to avoid oversizing (e.g. install only the equipment/capacity required for the first 15 years upon construction, and have the remaining capacity installed 15-years in into operation), where installing full equipment for 30-year future climate conditions would result in reduced performance on opening day, • Have all distribution networks (e.g. ductwork and piping) designed and constructed for 30-year future climate conditions from opening day, • Be ‘upgradeable’ at end of their design life to be adapted to changing climate projections. Future space requirements and access requirements should be considered and documented during design, • Be capable of maintaining the Standard Effective Temperature below 27°C, determined in accordance with ASHRAE 55 (2017), within the whole building (including suites) throughout the building service life, • Be capable of maintaining a maximum indoor temperature of 24°C (75.2°F) in amenity rooms and public spaces (excluding hallways) to be used as cool refuge spaces, • Prioritize mixed mode systems with tempered air wherever reasonable to reduce energy demands, increase resilience to power outage, and improve air quality. • Be electric and energy efficient (for mechanical heating and cooling systems) (e.g., heat pump). Window mounted air conditioning units are not permitted in design. Provide the source of future climate projections used in design. | Building Type: particularly relevant for multi-use residential buildings | Mechanical | For additional resources on this topic, refer to: • The BC Housing Design Guidelines and Construction Standards (BCH, 2019) • The Minimum Climate Resilience Standards for Public Sector Buildings (BC Ministry of Environment and Climate Change Strategy, in draft) • The Overheating Considerations for Existing Multi-Unit Residential Buildings Practice Advisory (EGBC, in draft, to be published in 2022) |  | Negative | - Including increased mechanical cooling in a building may increase both embodied and operational GHG emissions | Increase | Increase
3 | WILDFIRES & AIR QUALITY IMPACTS
Guiding Objectives: |  | ◊ Reduce wildfire risk to buildings through proactive planning, design, construction, and landscaping. ◊ Provide adequate indoor air quality across future outdoor air quality scenarios and conditions, and enable occupants to shelter in place during periods of poor outdoor air quality.
3.1. | Conduct a risk assessment to determine site-level wildfire risk, looking to wildland urban interface risk class maps provided by the Province. | If wildfire risk is rated as moderate or above, develop a Wildfire Risk Management Plan that demonstrates: • Site-level wildfire risk, • Assessed flammability of nearby vegetation and flammability considerations within landscape design, • Measures taken to include adequate fuel breaks and defensible space (at least 10m from forested areas, as per FireSmart), • Measures taken to select fire-resistant roofing and cladding materials, • Measures taken to improve fire resistance at building and parkade entry doors, • Careful landscape planning to include wildland vegetation buffers, reduced vegetation near buildings, and ongoing fuel management, • Measures taken to improve access and turnaround for fire suppression vehicles, and • Plans to quickly and safely evacuate building occupants if necessary. For buildings deemed to be at high risk, consult a relevant wildfire risk reduction expert for site-specific strategies. | Building Type: all residential building types. Risk Level: Plan only required for sites with a wildfire risk rating of moderate or above. | Planning | For additional resources on this topic, refer to: • FireSmart BC's guides and manuals database: https://firesmartbc.ca/resource-types/guides-manuals/ • FireSmart BC Landscaping Guide: https://firesmartbc.ca/wp-content/uploads/2021/04/FireSmartBC_LandscapingGuide_Web_v2.pdf • National Guide for Wildland-Urban Interface Fires (National Research Council Canada, 2021) • Wildfire-Resilience Best-Practice Checklist for Home Construction, Renovation and Landscaping (FireSmart Canada, 2022) |  | Low |  | Neutral | Neutral
3.2. | Develop an Air Quality Management Plan. | The Plan should be developed as part of construction/commissioning, and updated as needed throughout the buildings operation and lifecycle. The Plan should be tailored to each individual building and demonstrate: • Overall approach to maintaining indoor air quality to account for current conditions (i.e. business-as- usual, wildfires smoke, pandemic), • Maximum acceptable levels of indoor air contaminants in different areas of the building, • Measures in place to keep levels of indoor air contaminants below acceptable limits over building design life, and • Plans to stop work during construction due to air quality concerns. | Building Type: particularly relevant for multi-use residential buildings | Planning | For additional resources on this topic, refer to: • The Maintenance Matters Bulletin (BC Housing, in draft) | • Consider establishing specific targets regarding indoor air quality: carbon dioxide, volatile organic compounds, relative humidity, etc. | Moderate | Education, Energy Efficiency & Emissions Reductions: - Regular monitoring of indoor and outdoor indoor quality can help inform tenants on good times to employ natural ventilation, and thereby. - Reduce active ventilation energy load requirements. | Neutral | Decrease
3.3. | Provide filtered ventilation with 100% outdoor air supply air, so that indoor air contaminants and particulates do not exceed maximum levels for occupant wellbeing. | Design ventilation systems with heat recovery ventilators that: • Accommodate MERV 11 filters at all times, • Accommodate additional filters (e.g. MERV 13, MERV 15, activated carbon, electrostatic) capable of removing smoke particulate during wildfire smoke events, on a temporary and as-needed basis, and • Include fans with variable speed drives that are sized to overcome the additional pressure drop and energy consumption associated with these filters, when necessary. Provide good cross-flow to enable natural ventilation but ensure mechanical ventilation with filtration is available in all spaces in case of poor air quality event. Within the mechanical design report, provide a narrative that describes the approach to providing enhanced filtration for wildfire smoke events, including annotated drawings where appropriate. | Building Type: only relevant for multi-use residential buildings | Mechanical | For additional resources on this topic, refer to: • The Minimum Climate Resilience Standards for Public Sector Buildings (BC Ministry of Environment and Climate Change Strategy, in draft) • The Maintenance Matters Bulletin (BC Housing, in draft) | • Consider the merits and feasibility of having two ducts for central ventilation systems; one with a standard filtration (e.g. MERV 11) and one with higher efficiency filters installed (such as MERV 13 or above), which can be switched between as needed. • Consider defining a PM2.5 threshold for when higher filtration efficiencies (e.g. MERV 13) should be enacted. | Negative | - Additional filters may increase the friction losses and therefore increase the energy required to ventilate a spaces. | Neutral | Increase
3.4. | Locate air intakes to minimize intake of contaminants and summer heat. | Locate air intakes by taking into account the following considerations: • Locate air intakes in protected, well ventilated locations to minimize intake of contaminants (i.e. avoid pollutants near air intake locations, including plantings, parking areas, garbage disposal bins, and others), • Maintain at least 1.8 m (6 ft) separation between exhaust outlets and outdoor air intakes, • Locate parking exhaust louvers at least of 3 m (10 ft) from any operable window or fresh air intake, and • Where possible, locate air intakes in shaded areas and avoid areas subject to significant urban heat island effect, such as rooftops. Consider how urban heat island effect and roof heating effect may impact outdoor air intake temperatures and system design. Provide annotated drawings showing and describing air intake locations. | Building Type: all residential building types. | Mechanical | For additional resources on this topic, refer to: • The BC Housing Design Guidelines and Construction Standards (BCH, 2019) |  | Low |  | Neutral | Neutral
3.5. | Design building envelopes to minimize moisture exchange and limit exfiltration and infiltration of air, wildfire smoke, fine particulate matter (<2.5PM) and other air pollutants through materials of the assembly, joints in the assembly, joints in components of the wall assembly, and junctions with other building elements, including the roof. | Air barrier systems should include: • Fully adhered air barrier materials, such as self-adhered or liquid applied air barrier products (depending on the base structure), • Whole building air barrier testing and quality assurance testing of typical or complex air barrier system details during construction (see ASTM E783, ASTM E1186, and ASTM E2813-12 test standards), to help confirm efficacy, and • A Quality Control Plan with the general contractor for the air barrier system construction. Provide a narrative that describes approach to limiting exfiltration and infiltration through assembly, including annotated drawings as appropriate. | Building Type: only relevant for multi-use residential buildings | Envelope & Enclosure | For additional resources on this topic, refer to: • The Climate Change Considerations for Building Enclosure Engineers Practice Advisory (EGBC, 2022) |  | Low |  | Neutral | Neutral
3.6. | Conduct whole building air leakage testing prior to occupancy. | Perform post-construction airtightness testing in accordance with the BC Energy Step Code: • Recommended minimum whole building final airtightness testing target: 1.27L/s·m2 @75Pa, and • Recommended enhanced whole building final airtightness testing target: 1L/s·m2 @75Pa. In conjunction with this test, conduct an infrared scan to identify potential leakages and complete duct leakage testing. As part of the commissioning process, provide compliance report with modelling results, including narratives and annotated drawings as appropriate that summarize measures included to reduce air leakage. For infrared scan, include photographic evidence that the scan as been conducted. | Building Type: all residential building types. | Envelope & Enclosure | For additional resources on this topic, refer to: • The Minimum Climate Resilience Standards for Public Sector Buildings (BC Ministry of Environment and Climate Change Strategy, in draft) |  | Moderate |  | Neutral | Decrease
3.7. | Design suite partition walls to minimize air cross-contamination between suites (e.g. compartmentalize suites). | Design suite ventilation to be suite specific or from central systems directly ducted to suites (e.g. do not use pressurized corridors to ventilate suites). The suite entrance door should be properly sealed from hallway and/or outdoors. Conduct inter-suite air leakage testing prior to occupancy to limit inter-suite cross contamination: • Interior Partitions Air Leakage Rate (IPALR) should meet 1.2L/s/m2@50Pa; • Testing should be performed in accordance with ASTM E779; • Unit airtightness testing should be conducted to a minimum of 10% of total suites representing a variety of unit types. Where re-testing is required, due to failure to meet project requirement ratings, the failed suites should be retested, and for each failure 2 additional suites should be tested until all testing is positive and to the satisfaction of the Building Enclosure Consultant. As part of the commissioning process, provide compliance report with modelling results, including narratives and annotated drawings as appropriate that summarize measures included to reduce air leakage. | Building Type: only relevant for multi-unit residential buildings. | Envelope & Enclosure | For additional resources on this topic, refer to: • The BC Housing Design Guidelines and Construction Standards (BCH, 2019) | • Consider inter-suite cross contamination and impact of COVID-19 on central systems (both central heat or energy recovery ventilators and corridors). | Low |  | Neutral | Neutral
3.8. | Design vestibules around building entrances to limit infiltration. | Design multi-unit residential buildings with vestibules providing the following: • Double entries for high traffic areas to minimize smoke and particulate matter ingress in the event of adverse outdoor air quality, • A means to control pressure differential between building, vestibule and exterior, • Positive pressurization of vestibule relative to atmospheric pressure to minimize infiltration, and • A design that facilitates wayfinding, and movement by wheelchairs. Provide annotated drawings showing approach to vestibule design, and include a narrative of how pressurized vestibules will be tested in different seasons by pressure sensor or by tracer smoke. | Building Type: only relevant for multi-unit residential buildings. | Architecture |  |  | Low |  | Neutral | Neutral
3.9. | Factor indoor air quality concerns into selection of materials and finishes to prioritize building materials and furnishings (e.g. paints, carpets, glue, cleaning products for communal areas) that are low in volatile organic compounds. | Refer to the 2019 BC Housing Design Guidelines and Construction Standards for a complete list of low emitting material recommendations. Provide a materials selection list that highlights selection of low-emitting materials. | Building Type: all residential building types. | Planning | For additional resources on this topic, refer to: • The BC Housing Design Guidelines and Construction Standards (BCH, 2019) |  | Low |  | Neutral | Neutral
4 | FLOODING
Guiding Objectives: |  | ◊ Manage damage from flooding at both the building and on the site, including managing potential inflow from off-site sources. ◊ Protect the safety of building occupants and limit damage to key building systems (e.g. limit widespread contamination of building services and operations from floodwaters). ◊ Limiting negative impacts to neighbouring land uses and habitats.
4.1. | Conduct a hazard assessment to determine site-level flood hazard, along with any existing requirements (e.g. flood construction levels or FCL, minimum elevations). | The hazard assessment should include the following components: • Identify flooding issues that the site has experienced in the past, • For urban (pluvial) flooding, review local government documents for locally downscaled future climate data. Review the Provincial Stormwater Planning Guidebook for additional information on managing rainfall issues, • For riverine (fluvial) flooding, review Provincial and regional flood maps and evaluate the highest magnitude freshet flood events for present day, 2050 with climate change, and 2100 with climate change, and • For sea level rise, review local government documents and the Provincial Sea Level Rise Adaptation Primer, which recommends taking the following numbers into account for sea level rise: 0.5m for 2050, 1m for 2100 and 2m for 2200. Evaluate sea level rise needs alongside storm surge effect. Complete a hazard assessment report detailing the kinds of flooding the project is at risk of, as well as the sources of information used to derive conclusions. |  | Planning | For additional resources and best practices on this topic, refer to: • EGBC Legislated Flood Assessments in a Changing Climate in BC (EGBC, 2018) • Intact Centre for Climate Adaptation's Sample Flood Hazard Assessment (2018) https://www.intactcentreclimateadaptation.ca/wp-content/uploads/2019/12/final_assessment_report_Jan-2019-for-wide-circulation-Updated-Dec-19-19-1.pdf • Treading Water: Impact of Catastrophic Flooding on Canada's Housing Market (Intact Centre for Climate Adaptation, 2022) |  | Low |  | Neutral | Neutral
4.2. | Make careful siting and design decisions to locate main habitable areas above the flood construction level and avoid building new structures in high flood risk areas. Design building to remain largely functional during a flood event, even if spaces below flood construction level are unusable. | New multi-family buildings should not be located within fan or floodplain areas that are not protected by standard/adequate structural mitigation works unless: • The local government has adopted an appropriate bylaw or land use regulation that provides for building construction with knowledge of the flood hazard; or • The Qualified Professional (QP) concludes that the site may be suitable for the intended use. A QP may conclude that the site may be suitable for the intended use if at least one of the following conditions applies: • The building site is on an inactive fan, • A standard/adequate dike or equivalent other structural mitigation works is constructed with the pertinent approvals as part of the development, • The building site is not in a high hazard area of the fan or floodplain (as noted above and where safe access and egress is not possible), and • A risk assessment is undertaken whereby the local government establishes a tolerable level of flood risk, and the QP assessment confirms that the risk would be within this level. |  | Planning | For additional resources and best practices on this topic, refer to: • EGBC Legislated Flood Assessments in a Changing Climate in BC (EGBC, 2018) • EGBC Electrical Engineering Considerations in Flood-Resilient Design of Buildings (EGBC, 2020) |  | Low |  | Neutral | Neutral
4.3. | Develop a Flood Management Plan. | The Flood Management Plan should be developed at the planning and design and demonstrate the following: • Overall approach to flood mitigation (e.g. resist flooding, accommodate flooding), including direct and cascading impacts (e.g. fire-due-to-flood), • Current flood construction level (FCL) and design to withstand anticipated pressure and meet local government requirements, and • Approach to addressing increasing flooding in the future, both due to more frequent and severe urban/riverine events and sea level rise. If resisting flooding: • Design basements and structure and envelope below FCL to be waterproofed and/or watertight (i.e. tanked), and • Consider energy back-up measures if flooding occurs. If accommodating flooding: • Design buildings to maintain basic functions during the design flood event, • Protect key systems (i.e. electrical, mechanical) and services (e.g. elevator pits, circulation, back-up power) from flooding by locating above the FCL, • Identify areas that can be repurposed before, during and after flooding (e.g. for retention), • Plan to minimize effort and reduce time associated with water removal and clean-up (e.g. site grading, pumps, water-resistant materials), • Specify suitable materials in flood area for easy cleaning, repair or replacement, and • Protect occupant safety during flood events. |  | Planning | For additional resources and best practices on this topic, refer to: • Intact Centre for Climate Adaptation's Sample Flood Hazard Assessment (2018) https://www.intactcentreclimateadaptation.ca/wp-content/uploads/2019/12/final_assessment_report_Jan-2019-for-wide-circulation-Updated-Dec-19-19-1.pdf • Recommended Design Measures within the BC Housing MBAR Flood Resiliency Recommendations: https://www.horizoneng.ca/wordpress/wp-content/uploads/2020/12/Recommendations-Matrix-R8-QR.pdf |  | Low |  | Neutral | Neutral
4.4. | Develop a Stormwater Management Plan. | The Stormwater Management Plan should be developed at the planning and design phase and demonstrate how the project will: • Limit added stress on municipal stormwater infrastructure and nearby waterways and habitats from floodwater, sediment and contaminants. • Limit post-development 10-year flow rate from on-site discharged to the off-site storm sewer to be no greater than the 10-year pre-development flow rate, with pre-development flow rate based on 2014 IDF curves and post-development flow rate based on 2100 intensity-duration-frequency (IDF) curves to account for climate change, • Confirm that infiltration, capture and conveyance systems account for adjusted climate projections based on 100-year IDF curves for end of building life. Where site-specific updated future IDF curves do not exist, add 20% to rainfall intensity for a nominal factor of safety, • Capture and infiltrate 90% of average annual rainfall volume on site, and • Limit transference of sediment and contamination to neighbouring sites. |  | Planning | For additional resources and best practices on this topic, refer to: • Intact Centre for Climate Adaptation's Sample Flood Hazard Assessment (2018) https://www.intactcentreclimateadaptation.ca/wp-content/uploads/2019/12/final_assessment_report_Jan-2019-for-wide-circulation-Updated-Dec-19-19-1.pdf • University of Waterloo's IDF_CC Tool https://www.idf-cc-uwo.ca/ |  | Low |  | Neutral | Neutral
4.5. | Incorporate waterproofing strategies into below grade concrete in accordance with geotechnical conditions. | The project team should demonstrate how the following actions will be addressed: • Reduce water infiltration directly adjacent to the building foundation, especially if a below grade structure is present, • Apply moisture and vapour barriers to prevent moisture problems, and • Coordinate with all other building systems and penetrations. Provide a narrative that describes waterproofing strategies, including annotated drawings as appropriate. |  | Envelope & Enclosure | For additional resources and best practices on this topic, refer to: • Intact Centre for Climate Adaptation online resource database https://www.intactcentreclimateadaptation.ca/programs/home_flood_protect/resources/ • EGBC Climate Change Considerations for Building Enclosure Engineers (EGBC, 2022) • EGBC Geotechnical Engineering Services for Building Projects (EGBC, 2021) • BC Housing Building Guide to Site and Foundation Drainage for best practices: https://www.bchousing.org/research-centre/library/residential-design-construction/Builder-Guide-Site-and-Foundation-Drainage |  | Low |  | Neutral | Neutral
4.6. | Account for future climate projections in the design of roof drainage and rainwater leaders. | Capacity of roof drainage and rainwater leader design should be increased by an additional 20% above current municipal bylaw requirements. Provide a narrative within the mechanical design report discussing increased stormwater capacity, along with annotated drawings. |  | Mechanical | For additional resources and best practices on this topic, refer to: • Intact Centre for Climate Adaptation online resource database https://www.intactcentreclimateadaptation.ca/programs/home_flood_protect/resources/ |  | Low |  | Neutral | Neutral
4.7. | Include provisions to protect against flooding of flat roof areas if primary drainage system becomes clogged. | Provide a narrative within the mechanical design report that describes approach to roof drainage, including annotated drawings as appropriate. |  | Architecture | For additional resources and best practices on this topic, refer to: • Intact Centre for Climate Adaptation online resource database https://www.intactcentreclimateadaptation.ca/programs/home_flood_protect/resources/ |  | Low |  | Neutral | Neutral
4.8. | Use site grading to direct water away from buildings, and permeable paving materials to improve overall rainwater infiltration capacity of the site. | Provide a landscaping plan with narratives and annotated drawings as appropriate. Note that permeable pavers need to be properly maintained for continued infiltration. |  | Landscape |  |  | Low |  | Neutral | Neutral
5 | SEISMIC EVENTS & SLOPE HAZARDS
Guiding Objectives: |  | ◊ Protect occupant life and safety during and following seismic events. Maximize the ability of building occupants to shelter in place during and following seismic events. ◊ Minimize structural damage to the building and building systems (e.g. mechanical and electrical systems) that may result from various seismic events or slope hazard events. ◊ Limit the risk of fires, dike failure and floods, and other cascading impacts that may result from a seismic event. ◊ Facilitate rapid assessment of the building following seismic events. ◊ Decrease time and cost required to repair the building following seismic events.
5.1. | Conduct a hazard assessment to determine site-level seismic hazard, along with any existing requirements (e.g. building codes or jurisdictional). | In addition to any code requirements, consider soil type, groundwater level, and liquefaction potential. Complete a risk assessment report detailing site-level seismic risk, as well as the sources of information used to derive conclusions. |  | Planning |  |  | Low |  | Neutral | Neutral
5.2. | Designate a space for outdoor assembly during especially large seismic events. | Provide a narrative and annotated drawings as appropriate. |  | Planning |  |  | Low |  | Neutral | Neutral
5.3. | Include measures to help the building withstand seismic events. | For large buildings, examples include but are not limited to: • Mass timber construction, • Sheer walls, • Braced frames, • Base isolation, or • Energy dissipating devices. For low-rise wood-frame buildings, confirm that the sill plate is bolted to the foundation. Provide a narrative that describes approach to enhancing seismic resilience, including annotated drawings as appropriate. |  | Structural |  |  | Low |  | Neutral | Neutral
5.4. | Investigate the stability of the building site and surrounding soils and underlying geology. | Demonstrate that any steep-slope (≥ 15% or 6.75⁰) soils and underlying geology on the building site and uphill from the building site have been investigated through a signed report from a geotechnical engineer. | Risk Level: Only relevant for sites near steep slopes | Geotechnical |  |  | Low |  | Neutral | Neutral
5.5. | Include measures to reinforce pipe joints and bracing to withstand breakage and leaks during seismic events. | Provide a narrative and annotated drawings as appropriate. |  | Mechanical |  |  | Low |  | Neutral | Neutral
5.6. | Include shutoff valves for all natural gas lines and water lines to limit the risk of fires and flooding that may result from line ruptures. | Provide procedure on how utilities will be restored quickly and safely after seismic events, with a narrative and annotated drawings as appropriate. |  | Mechanical |  |  | Low |  | Neutral | Neutral
5.7. | Introduce a process for alerting occupants when they are able to re-renter the building, accounting for the risk of aftershocks. | Train building staff to conduct Rapid Damage Assessments and Post-Disaster Building Assessments. Install strong motion instrumentation to provide building performance data that to augment visual assessment. Retain an engineer to fully inspect the building within three days following a seismic event. Provide on-site and off-site drawings of critical components to inspect to inform re-entry. Provide a narrative that describes approach to post-earthquake assessments, communications and inspections. | Building Type: only relevant for multi-unit residential buildings. | Operations |  |  | Low |  | Neutral | Neutral
6 | POWER OUTAGE
Guiding Objectives: |  | ◊ Protect the safety of building occupants during a power outage. ◊ Limit damage to key building systems and services. ◊ Reduce reliance on utility providers through renewable energy generation and battery storage.
6.1. | Develop an Emergency Power Supply Management Plan. | The Plan should identify and prioritize: • Power requirements for different parts of the building, • Critical and non-critical loads throughout the building, including building systems, • Approach to providing back-up power and fuel to allow the building to operate for at least 72 hours in the event of an emergency, as per the City of Toronto Minimum Backup Power Guidelines for MURBs, and • Approach to ensuring redundancy in back-up power for critical systems, and • Approach to ensuring that back-up power sources are resilient to climate-related hazards (e.g. extreme heat events, flooding). Buildings with strong enclosure performance and airtightness can stay comfortable and livable for days without power. Power Supply Management Plans for these buildings should include one back-up power system connected to critical services and refuge spaces. Buildings that are 6-storeys or more and/or have poor enclosure performance and airtightness should include redundant back-up power (i.e. minimum of two back-up power systems and required fuel). | Building Performance: Buildings with poorer enclosure performance and airtightness require more redundant back-up systems | Planning |  |  | Low |  | Neutral | Neutral
6.2. | Conduct pre-development modelling and post-development testing to strengthen the efficacy of back-up power systems. | The following should be addressed in the pre-development modelling and post-development testing: • Within the energy model, simulate a power outage and demonstrate building conditions under this scenario (e.g. power usage, temperature), • Design interiors to not exceed defined maximum temperatures for different areas of the building (as per ASHRAE 55) under future climate scenarios (e.g. RCP8.5 in 2050) during back-up power operation, • Design interiors to not drop below minimum temperatures for different areas of the building during cold snaps during back-up power operation, and • Perform monthly testing of generators. Provide modelling results with narratives and annotated drawings as appropriate that summarize building conditions during a power outage. |  | Planning |  |  | Low |  | Neutral | Neutral
6.3. | Conduct a site-wide renewable energy feasibility study to assess power supply, availability and renewable energy options. The building and site structures should be designed to be 'solar ready' and 'battery ready'. | Solar ready' and 'battery ready' are defined below: Solar-ready: • All distribution networks, including but not limited to ductwork and piping, are designed to accommodate the installation of solar panels, even if installation does not take place at the time of construction, and • Design site structures to have access to a power supply. Battery-ready: • Design for easy installation of batteries in the future by considering future space and location requirements for on-site battery storage. Provide study results with narratives and annotated drawings as appropriate. |  | Planning |  |  | Moderate | Energy Efficiency & Emissions Reductions: - Onsite renewable energy and battery storage may reduce operational GHG emissions, particularly if it is able to replace diesel back-up generators. | Neutral | Decrease
6.4. | Design building management systems (BMS) and/or electrical infrastructure to allow for segregation of loads. | Provide a narrative that describes the approach to load segregation. | Building Type: only relevant for multi-unit residential buildings. | Electrical |  |  | Low |  | Neutral | Neutral
6.5. | Maintain a means of external communication that does not rely on grid power. | Maintain at least one conventional land-line telephone to be used in case of power outage. Alternatively, provide one of the following alternate communication devices along with training for staff and residents on how to effectively use them during an emergency: satellite phone, citizen band (CB) radio, or amateur (HAM) radio. Provide a narrative that describes approach to communications during a power outage. |  | Operations |  |  | Low |  | Neutral | Neutral
7 | WIND & STORMS
Guiding Objectives: |  | ◊ Limit damage to the building and potential risks to users that may result from high winds and storms.
7.1. | Conduct a site-wide Wind Study that includes all buildings. | The Study should demonstrate: • How the project has considered present and future wind velocities based on data provided by climate science authorities (e.g. PCIC), noting that wind projections will vary greatly; In this, do not assume that a current safety factor amounts to future-proofing for extreme events, • Assumed forces and wind pressures for base building design, cladding design, sections and roofs, • Potential hazard areas and features (e.g. trees, overhangs), • Measures in place to keep building materials and site elements (e.g. lighting, signage, exterior shades, canopies) secure, so that they do not become projectiles during extreme wind events, • Areas where impact-resistant materials could be used, and • Implications for rooftop equipment and renewable energy systems (e.g. solar photovoltaic (PV) panels). Note that if wind study results are more onerous than the BC Building Code, this study should take precedence. Provide wind study results with narratives and annotated drawings as appropriate that summarize measures to mitigate wind risk. | Building Type: only relevant for multi-unit residential buildings. | Planning |  |  | Low |  | Neutral | Neutral
7.2. | If wind speed thresholds are projected to be exceeded, include site-level measures to protect pedestrians (e.g. wind breaks, buffers) and access areas (e.g. loading docks, door assemblies, vestibules). | Provide a narrative and annotated drawings as appropriate. |  | Architectural |  |  | Low |  | Neutral | Neutral
7.3. | When locating equipment on the roof cannot be avoided, secure rooftop equipment and underlying membranes to withstand future climate projections and wind loads. | All rooftop equipment should be constructed to withstand the year 2050 wind loads as per future climate projections. Approaches should include installation of protective barriers and bolting down of all equipment. Install a waterproof membrane under sloped roof cover to provide protection if rooftop appurtenances blow away in the wind. Provide narrative and annotated drawings as appropriate. | Building Type: only relevant for multi-unit residential buildings. | Mechanical |  |  | Low |  | Neutral | Neutral
8 | SNOWFALL
Guiding Objectives: |  | ◊ Allow for quick and safe management of snow after a major snowfall event, both current and projected.
8.1. | Conduct a site-wide Snow Study that includes all buildings. | The Study should demonstrate: • How the project has considered historic and future snowfall projections (i.e. likely range of snowfall increase or decrease), • How the project will account for changing properties of future snowfall (e.g. heavier/wetter snowfall in some areas), and • Consideration of the impacts of wind exposure and snow drifting, and how to protect pedestrian movement and accessibility of spaces. Provide snow study results with narratives and annotated drawings as appropriate. |  | Planning |  |  | Low |  | Neutral | Neutral
8.2. | Develop a site-wide Snow Management and Safety Plan. | The Plan should demonstrate: • Approach to snowfall clearing to allow safe access and movement around the site, • Confirmation of whether the building has its own equipment/resources or will rely on an external contractor, • Identification of locations where snow will be stockpiled, and • Approach to addressing snow and icicles falling off roofs, and potentially creating a hazard for pedestrians and blocking entrances. The Plan should include: • Whether snow can be safely removed from the roof in a timely manner, • Confirmation that the Plan does not create unbalanced snow loads , • Occupational health and safety and fall protection requirements, • How and when retrofit structural evaluations and strengthening are required when a roof is found to need frequent snow/ice removal, and • Barrier placement to protect the public, if required. | Building Type: only relevant for multi-unit residential buildings. | Planning |  |  | Low |  | Neutral | Neutral
9 | WATER SHORTAGE & DROUGHT
Guiding Objectives: |  | ◊ Design for maximum water efficiency and water reuse to minimize disruption and allow continued operations during water shortage and/or drought.
9.1. | Develop an Emergency Water Shortage Plan. | The Plan should be developed at the building planning and design stage and demonstrate: • Risk assessment of compromised water supply and/or lower water pressure under different future climate scenarios, • Water conversation measures to reduce demand, and • Appropriate amount of on-site storage for potable and process water, including potential for rain/grey water systems. |  | Planning | Note that there are existing guidelines on how to approach greywater and construct buildings to be greywater-ready: • Health Canada. (2010). Canadian Guidelines for Domestic Reclaimed Water for Use in Toilet & Urinal Flushing. • CAN/CSA-B128.1-06/B128.2-06 Update 1 |  | Low |  | Neutral | Neutral
9.2. | Design for maximum water efficiency and water reuse to minimize disruption and allow continued operations during water shortage and/or drought. |  |  | Mechanical |  |  | Low |  | Neutral | Neutral
9.3. | Provide landscape plans demonstrating how the project will reduce potable water used for irrigation. | The landscape plan should demonstrate how the project will reduce potable water used for irrigation, covering topics such as maintenance, water availability, irrigation methods. If used, all extensive green roof areas are to have low maintenance requirements and be appropriate for the micro-climate of each roof area. |  | Landscape |  |  | Low |  | Neutral | Neutral
9.4. | For all plantings, select plants that are non-invasive and drought-tolerant, and that generate limited pollen. | Within landscape plans, provide plant list that explains plant selection, along with narrative illustrating pathway towards 40% natural canopy coverage. |  | Landscape |  |  | Low |  | Neutral | Neutral
10 | MOISTURE & HUMIDITY
Guiding Objectives: |  | ◊ Limit damage to building materials from moisture and/or humidity ingress.
10.1. | Size HVAC equipment to account for future humidity loads and rather than historical conditions. Consider alternate methods of dehumidification (e.g. desiccation) to reduce loads on equipment. | Within the mechanical design report, provide a narrative that describes the approach to managing humidity loads, including annotated drawings as appropriate. |  | Mechanical |  |  | Low |  | Neutral | Neutral
10.2. | Design for healthy relative indoor humidity levels in present and future climate conditions. | Design for relative indoor humidity of between 30% and 50% (note that code dictates 30-60%), using future climate projections to guide design. Within the mechanical design report, provide a narrative that describes the approach to maintaining relative indoor humidity between the specified range. |  | Mechanical |  |  | Low |  | Neutral | Neutral
10.3. | Demonstrate how condensation will be passively managed throughout the building envelope and under future climate conditions over the lifespan of the building. | Provide a narrative that describes the approach to managing condensation, including annotated drawings as appropriate. |  | Envelope & Enclosure |  |  | Moderate | Materials Management: - Ensuring proper moisture management with building materials may extend the life of the materials, thereby reducing embodied GHG emissions associated with the building. | Decrease | Neutral
11 | FREEZE/THAW
Guiding Objectives: |  | ◊ Minimize damage from freeze/thaw cycles.
11.1. | In areas where permafrost is a consideration, carry out a study of impacts to permafrost due to climate change and document overall approach to permafrost management and ensuring structural stability: a) Keep soil frozen b) Keep soil thawed c) Isolate project from active layer | Provide permafrost study results with narratives and annotated drawings as appropriate that summarize measures to protect structural stability. | Risk level: only relevant for areas that experience permafrost. | Structural |  |  | Moderate | Materials Management: - Avoiding excess humidity within building materials may extend the life of the materials, thereby reducing embodied GHG emissions associated with the building. | Decrease | Neutral
11.2. | Use high-performance insulation and air sealing to eliminate the escape of heat from conditioned areas. Locate exhaust away from enclosure materials which are susceptible to high humidity micro-climates. | Verify high-performance insulation at time of construction, working closely with contractor to confirm that proper materials and practices are used. |  | Envelope & Enclosure |  |  | Moderate | Materials Management: - Avoiding excess humidity within building materials may extend the life of the materials, thereby reducing embodied GHG emissions associated with the building. | Decrease | Neutral
12 | SOCIAL DIMENSIONS
Guiding Objectives: |  | ◊ Design the site and building layout to help bring together neighbours of all different ages and backgrounds by encouraging spontaneous interactions and collaborative activities. ◊ Plan for building-scale operations and programming measures to help increase social connectedness, make the building feel more like home, and provide a safety network for all residents. ◊ Share important information effectively across a range of mediums to meet the unique needs of different building occupants (i.e. universal communication). ◊ In case of emergency, help people have the space and supplies they need to remain in their building safely and with a degree of comfort for at least three days, and to evacuate safely if necessary. ◊ Help encourage people in the building to be more informed, knowledgeable, and better equipped to collectively respond during emergency situations. ◊ Design & operate the building to help further social equity in the community and provide benefit to a wide variety of people. ◊ Plan for measures at the building scale to enhance long-term resilience in the surrounding neighbourhood and across the community as a whole.
12.1. | During the early design or redevelopment of a building, utilize a collaborative and inclusive integrated design process (IDP) that engages affected stakeholders, rights and title holders, and partners (e.g. residents, neighbours, local Indigenous peoples, nearby businesses and workers, etc.). | Provide confirmation that the project team has employed IDP, along with supporting documentation. | Building Type: only relevant for multi-unit residential buildings. | Planning |  |  | Low |  | Neutral | Neutral
12.2. | Work with and across local communities to establish Indigenous design guidelines and principles that support decolonization and reconciliation. | Provide finalized Indigenous design guidelines that have been endorsed by the groups involved. | Building Type: only relevant for multi-unit residential buildings. | Reconciliation |  |  | Low |  | Neutral | Neutral
12.3. | Work with community organizations to determine where neighbourhood resilience hubs are or should be. If possible, establish the building as a community resilience space to act as a neighbourhood hub (see Urban Sustainability Directors Network (USDN) - Resilience Hubs for more information). | Provide a narrative that describes approach to establishing a community resilience hub, including annotated drawings as appropriate. | Building Type: only relevant for multi-unit residential buildings. | Planning |  |  | Low |  | Neutral | Neutral
12.4. | Enable the building to support a variety of family sizes by including increased numbers of two- and three-bedroom units. | Provide a narrative that describes housing unit composition, including annotated drawings as appropriate. | Building Type: only relevant for multi-unit residential buildings. | General Resilience |  |  | Low |  | Neutral | Neutral
12.5. | Go beyond code in both number of and design of adaptable housing units, universally accessible units and visitable units. | Provide a narrative that describes accessible unit composition, including annotated drawings as appropriate. | Building Type: only relevant for multi-unit residential buildings. | General Resilience |  |  | Low |  | Neutral | Neutral
12.6. | Establish a designated amenity space that includes the essentials needed to host social events (e.g. chairs, tables). | Provide a narrative that describes utilization of an amenity space for social functions, including annotated drawings as appropriate. | Building Type: only relevant for multi-unit residential buildings. | Social Connection |  |  | Low |  | Neutral | Neutral
12.7. | Establish an Emergency Management Plan in consultation with building occupants, ensuring that it is appropriate to building size. |  | Building Type: only relevant for multi-unit residential buildings. | Resident Preparedness |  |  | Low |  | Neutral | Neutral
12.8. | Consider the needs of people with disabilities when exiting in an emergency (i.e. wheelchair accessible exits, well marked areas of refuge, stairwells designed to guide people with low vision). | Provide a narrative that describes emergency evacuation procedures for all residents, including people with disabilities, including annotated drawings as appropriate. |  | Resident Preparedness |  |  | Low |  | Neutral | Neutral
12.9. | Conduct building tours with new residents and staff so that people are familiar with the space during emergency situations. If this is not possible, provide video or picture guides to the building's features. | Provide a narrative that describes approach to building orientation for new residents. | Building Type: only relevant for multi-unit residential buildings. | Resident Preparedness |  |  | Low |  | Neutral | Neutral
12.10. | Use a bulletin board in a common area to share relevant safety and emergency messaging, and post information in accessible formats (e.g. large print). Display or distribute written materials in multiple languages according to building occupancy. | Provide a narrative that describes approach to safety and emergency communications. | Building Type: only relevant for multi-unit residential buildings. | Resident Preparedness |  |  | Low |  | Neutral | Neutral
12.11. | Install a variety of emergency alert systems (e.g. fire bells, strobe lights, beacons, raised lettering) to notify all residents of the building, including those with hearing or vision impairments. | Provide a narrative that describes approach to safety and emergency communications. |  | Resident Preparedness |  |  | Low |  | Neutral | Neutral
© BC Housing 2022
Climate-ready Housing Design Guide V1
CLIMATE RESILIENCE APPROACHES AND STANDARDS
This sheet describes recommended resilience design approaches and technical standards. 12 resilience categories are covered: (1) General Resilience, (2) Warmer Temperatures & Extreme Heat, (3) Wildfires & Air Quality Impacts, (4) Flooding, (5) Seismic Events & Slope Hazards, (6) Power Outage, (7) Wind & Storms, (8) Snowfall, (9) Water Shortage & Drought, (10) Moisture & Humidity, (11) Freeze Thaw, (12) Social Resilience & Reconciliation.
Each resilience design approach and technical standard has also been evaluated with respect to its low carbon resilience (LCR) potential, as well as its relationship with embodied and operational greenhouse gas emissions.
The first three categories (General Resilience, Warmer Temperatures & Extreme Heat, and Wildfires & Air Quality Impacts) are the primary focus of this iteration of the Guide and their technical standards have been developed in detail to align with and build on other provincial and national technical standards in place or under development (refer to column G for sources). Categories 3 to 12 include draft technical standards developed at a high level only; further work is required in future iterations of the Guide to match the level of detail provided in the first three categories.
MORE DETAILED & COMPLETE TECHNICAL STANDARDS
MORE PRELIMINARY TECHNICAL STANDARDS

## Resilient Design Strategies
RECOMMENDED RESILIENT DESIGN STRATEGIES
SOURCE | RESILIENT DESIGN STRATEGY | PRIMARY HAZARD | REQUIREMENT CATEGORY | SCALE | LEAD TEAM | IMPACT ON GHG EMISSIONS REDUCTIONS (Positive / Neutral / Negative) | IMPACT ON SEISMIC RESILIENCE (Positive / Neutral / Negative) | IMPACT ON PANDEMIC RESILIENCE (Positive / Neutral / Negative) | LCR POTENTIAL (Negative / Low / Moderate / High) | COMMENTARY ON INTERACTION BETWEEN RESILIENCE & GHG EMISSIONS REDUCTIONS | EMBODIED EMISSIONS (Decrease/Neutral/Increase) | OPERATIONAL EMISSIONS (Decrease/Neutral/Increase)
ASEC | Establish a maintenance schedule for building assets as part of the design for durability. Ensure that a maintenance manual for the building is made available for the people responsible for its maintenance. | General | General Resilience | Building | Owner/Operator | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
ASEC | Conduct routine maintenance inspections to detect prevailing and emerging risks to building resilience. | General | General Resilience | Building | Owner/Operator | Neutral | Positive | Positive | Low |  | Neutral | Neutral
HCDG | Explore opportunities to emphasize role of the building as a cooling centre and/or community resilience hub. | Warming Temperatures & Extreme Heat | General Resilience | Off-site | Owner/Operator | Neutral | Positive | Positive | Low | - Providing active cooling to a space may increase emissions; however if a community cooled space is used instead of individually cooling each suite, this may decrease emissions. | Neutral | Decrease
| Install a weather station on site at least one year prior to construction, to provide local weather information for modelling. | Warming Temperatures & Extreme Heat | General Resilience | Site | Owner/Operator | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Allow extra space, pipe, coil or ductwork allotment for future mechanical cooling equipment. | Warming Temperatures & Extreme Heat | Mechanical | Building | Mechanical | Negative | Neutral | Positive | Negative | - Allowing for extra space for ductwork and mechanical equipment will either (a) reduce the ceiling height in the spaces (no effect on carbon emissions) or (b) increase the overall height of the building (increasing the embodied emissions within the building). | Increase | Neutral
HCDG | Carefully consider the tension between over- and under-sizing equipment. Use modular and/or scalable mechanical units for critical equipment, functions or areas. | Warming Temperatures & Extreme Heat | Mechanical | Building | Mechanical | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Ensure that mechanical systems can provide real-time feedback that allow the end user to manually modulate the system. | Warming Temperatures & Extreme Heat | Mechanical | Building | Mechanical | Neutral | Neutral | Positive | Low | - Providing user control may decrease excessive cooling in the summer. | Neutral | Decrease
NYC | Where feasible, locate heat-generating equipment (e.g. transformers, switchgear) outdoors. | Warming Temperatures & Extreme Heat | Mechanical | Building | Mechanical | Neutral | Neutral | Neutral | Low | - In buildings with active cooling, this may decrease cooling demand in the summer. | Neutral | Decrease
NYC | Split building cooling loads across different HVAC systems for redundancy and improved multi-zone control. | Warming Temperatures & Extreme Heat | Mechanical | Building | Mechanical | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Ensure that pipes are easy to access for future upgrades and include provisions for future connections (e.g. flanges, tied-in valves). | Warming Temperatures & Extreme Heat | Mechanical | Building | Plumbing | Neutral | Positive | Positive | Low |  | Neutral | Neutral
HCDG | Use high-albedo building materials (e.g. white materials for roofs) to reduce envelope surface temperatures. | Warming Temperatures & Extreme Heat | Envelope & Enclosure | Building | Architect | Positive | Neutral | Neutral | Moderate | Energy Efficiency & Emissions Reductions: - Reduce cooling demands/summer heat gains. - Using high albedo materials may decrease cooling demands in the summer (reducing GHG emissions or the requirement for cooling). - It may also increase heating demand in the winter, although much less significantly as there are generally fewer sunny days in the winter. | Neutral | Decrease
HCDG | Reduce window-to-wall ratios (WWR), balancing the need for natural light and energy efficiency. | Warming Temperatures & Extreme Heat | Envelope & Enclosure | Building | Architect | Positive | Neutral | Neutral | High | Energy Efficiency & Emissions Reductions: - Reduce cooling demands/summer heat gains. - Reduce winter heat losses. - Decreasing heat loss in the winter and heat gains in the summer may reduce GHG emissions. | Neutral | Decrease
HCDG | Use high-efficiency triple-glazed windows with low solar heat gain coefficients to improve thermal comfort. | Warming Temperatures & Extreme Heat | Envelope & Enclosure | Building | Envelope | Positive | Neutral | Neutral | Moderate | Energy Efficiency & Emissions Reductions: - Reduce cooling demands/summer heat gains. - Reduce winter heat losses. - Decreasing heat loss in the winter and heat gains in the summer may reduce GHG emissions. | Increase | Decrease
MBAR | Educate occupants on practices to keep cool, including closing windows after noon and opening them at night. | Warming Temperatures & Extreme Heat | Operations | Building | Owner/Operator | Positive | Neutral | Positive | High | Education: - Education can reduce heat gains and demands on cooling systems. | Neutral | Decrease
MBAR | Develop training programs to inform staff at what temperatures they should begin checking on lone occupants and help staff to be able to identify symptoms of heat stress and associated health complications. | Warming Temperatures & Extreme Heat | Operations | Building | Owner/Operator | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Include passive design measures that encourage natural ventilation (e.g. use both high and low windows). Locate operable windows in strategic locations for back-up cooling and night purge, noting that night purge will become less effective over time as overnight temperatures increase. | Warming Temperatures & Extreme Heat | Architectural | Building | Architect | Positive | Neutral | Positive | High | Energy Efficiency & Emissions Reductions: - Reduce active ventilation energy load requirements. - Using mixed mode or pure natural ventilation may decrease energy requirements for ventilation, particularly during shoulder season and warmer months. | Neutral | Decrease
HCDG | Provide exterior shading (both passive and active), especially for glazing on south and west facades. | Warming Temperatures & Extreme Heat | Architectural | Building | Architect | Positive | Neutral | Neutral | High | Energy Efficiency & Emissions Reductions: - Reduce cooling demands/summer heat gains. - Well designed shades may decrease the heat gains to the building in the summer without significantly impacting them in the winter. | Increase | Decrease
HCDG | Where appropriate considering future climate conditions, employ thermal mass strategies for passive cooling. | Warming Temperatures & Extreme Heat | Architectural | Building | Architect | Neutral | Neutral | Positive | Low | Energy Efficiency & Emissions Reductions: - Reduce cooling demands/summer heat gains. - Reduce winter heat losses. - Depending on the material used for the thermal mass, this strategy may involve an increase in embodied emissions while there may be a decrease in operational emissions. | Increase | Decrease
HCDG | Orient buildings and open spaces to maximize passive cooling (e.g. layout and form that encourages natural airflow). | Warming Temperatures & Extreme Heat | Architectural | Building | Architect | Positive | Neutral | Positive | High | Energy Efficiency & Emissions Reductions: - Reduce active ventilation energy load requirements. - Using mixed mode or pure natural ventilation may decrease energy requirements for ventilation, particularly during shoulder season and warmer months. | Neutral | Decrease
HCDG | Provide dedicated storage room(s) for critical spare parts and supplies (e.g. chiller components, filters). | Warming Temperatures & Extreme Heat | Architectural | Building | Architect | Neutral | Positive | Positive | Low |  | Increase | Neutral
HCDG | Reserve space adjacent to buildings and across the site for future mechanical equipment. | Warming Temperatures & Extreme Heat | Architectural | Site | Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Use biophilic design (i.e. design that increases occupant connectivity to the natural environment) to complement cooling strategies and promote positive health outcomes for occupants. | Warming Temperatures & Extreme Heat | Landscape | Building | Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Utilize local, heat- and drought-tolerant planting, and low-pollen trees to optimize shading across the site. | Warming Temperatures & Extreme Heat | Landscape | Site | Landscape Architect | Neutral | Neutral | Neutral | Moderate | Energy Efficiency & Emissions Reductions: - Reduce cooling demands/summer heat gains. - Optimizing shading may decrease cooling requirements. - Using drought resistant plants may reduce water demand. | Neutral | Decrease
HCDG | Minimize heat absorbing surfaces in open spaces with low-pollen planting. | Warming Temperatures & Extreme Heat | Landscape | Site | Landscape Architect | Positive | Neutral | Neutral | Moderate | Energy Efficiency & Emissions Reductions: - Reduce cooling demands/summer heat gains. | Neutral | Decrease
HCDG | Provide exterior areas of respite under tree canopy. | Warming Temperatures & Extreme Heat | Landscape | Site | Landscape Architect | Neutral | Neutral | Positive | Low |  | Neutral | Neutral
HCDG | Inventory and reduce areas that contribute to the urban heat island effect. | Warming Temperatures & Extreme Heat | Landscape | Site | Landscape Architect | Positive | Neutral | Neutral | Moderate | Energy Efficiency & Emissions Reductions: - Reduce cooling demands/summer heat gains. | Neutral | Decrease
HCDG | Utilize high-albedo paving on walkways and parking areas. | Warming Temperatures & Extreme Heat | Landscape | Site | Landscape Architect | Neutral | Neutral | Neutral | Moderate | Energy Efficiency & Emissions Reductions: - Reduce cooling demands/summer heat gains. | Neutral | Decrease
HCDG | Use enhanced sealing for filters and bypass systems to eliminate gaps that reduce effectiveness. Plan for duct air leakage testing and commissioning. | Wildfires & Air Quality Impacts | Mechanical | Building | Mechanical | Positive | Neutral | Positive | Moderate | Energy Efficiency & Emissions Reductions: - Reduce active ventilation energy load requirements. - Using mixed mode or pure natural ventilation may decrease energy requirements for ventilation, particularly during shoulder season and warmer months. | Neutral | Decrease
HCDG | Consider significantly enhanced airflow capability for 'pandemic mode'. | Wildfires & Air Quality Impacts | Mechanical | Building | Mechanical | Negative | Neutral | Positive | Negative | - Increasing the ventilation load requirement may increase GHG emissions | Neutral | Increase
HCDG | Consider displacement or separate system for outside air ventilation to improve ventilation effectiveness. Intention is to deliver highest quality air close to people and removing contaminants out of breathing zone. | Wildfires & Air Quality Impacts | Mechanical | Building | Mechanical | Positive | Neutral | Positive | Moderate | Energy Efficiency & Emissions Reductions: - Reduce active ventilation energy load requirements. - The advantages of displacement ventilation (DV) can include a reduction in cooling energy, longer free-cooling periods, better air quality than traditional HVAC systems, and a reduction in ventilation air requirements. These benefits are climate and building specific, and DV may not be appropriate outside of relatively mild climates with low cooling loads. | Neutral | Decrease
HCDG | Design for colder months by including mechanical ventilation via high-efficiency ERVs to allow higher levels of outside air in peak influenza season. Ensure that system does not contribute to cross-flow contamination. | Wildfires & Air Quality Impacts | Mechanical | Building | Mechanical | Negative | Neutral | Positive | Low |  | Neutral | Neutral
HCDG | Use non-recirculating air systems where possible with high levels of heat recovery, | Wildfires & Air Quality Impacts | Mechanical | Building | Mechanical | Positive | Neutral | Positive | Moderate | Energy Efficiency & Emissions Reductions: - Reduce cooling demands/summer heat gains. - Reduce winter heat losses. | Neutral | Decrease
MBAR | Eliminate infiltration of air from the parking garage into the building using air barriers and ventilation. | Wildfires & Air Quality Impacts | Mechanical | Building | Mechanical | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
MBAR | Install electric (not gas) cooking appliances. If using gas appliances, ensure sufficient ventilation in cooking areas to reduce particulate matter exposure. | Wildfires & Air Quality Impacts | Mechanical | Building | Mechanical | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
CapU | For above and below ground mechanical cables, use rigid metallic conduits to make the system less susceptible to the extreme heat that can result from a wildfire. | Wildfires & Air Quality Impacts | Mechanical | Site | Mechanical | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
CapU | Choose building and parkade entry doors that are fire-rated and sealed with an air barrier. | Wildfires & Air Quality Impacts | Envelope & Enclosure | Building | Envelope | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Explore opportunities to clean filters (e.g. roll filters, including grade of prefilters to deal with smoke and pollen particulate). | Wildfires & Air Quality Impacts | Operations | Building | Mechanical | Positive | Neutral | Positive | High | Energy Efficiency & Emissions Reductions: - Reduce active ventilation energy load requirements. | Neutral | Decrease
MBAR | In high wildfire risk areas, use non combustible cladding, roofing materials and mesh debris screens for gutters, eaves and vents to reduce accumulation of flammable materials | Wildfires & Air Quality Impacts | Operations | Building | Owner/Operator | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Allow for 100% recirculation capacity or 'wildfire mode' that can be employed for short periods of time, which requires that the building is almost leak free and ventilation system has carbon filter capability. | Wildfires & Air Quality Impacts | Mechanical | Building | Mechanical | Neutral | Neutral | Positive | Low | Energy Efficiency & Emissions Reductions: - Switching to 100% indoor air may reduce summer cooling loads and winter heating loads. | Neutral | Neutral
MBAR | Develop a whole-building strategy to manage moisture and mould by reducing wet or damp areas, standing water, and condensation (minimizing attraction for mosquitos and other insects). | Wildfires & Air Quality Impacts | Operations | Building | Owner/Operator | Neutral | Neutral | Neutral | Low | Materials Management: - Managing moisture and mould may decrease the required frequency of repairs and retired building materials. | Decrease | Neutral
HCDG | Allocate space both near equipment and elsewhere in the building for storage and stockpiles of enhanced filters (e.g. carbon, MERV 14, HEPA). | Wildfires & Air Quality Impacts | Architectural | Building | Architect | Neutral | Neutral | Positive | Low |  | Neutral | Neutral
HCDG | Use natural ventilation for extended periods of year (i.e. spring, summer, fall), which is made possible in buildings with high-performance insulation. Provide operable windows in suites, to cut mechanical supply to the room but still allow for kitchen and bathroom exhaust. Provide a red light/green light system at the window to warn when it should not be opened (e.g. high smoke or wind events). | Wildfires & Air Quality Impacts | Architectural | Building | Architect | Positive | Neutral | Positive | High | Energy Efficiency & Emissions Reductions: - Reduce active ventilation energy load requirements. | Neutral | Decrease
HCDG | Minimize sources of pollutants near air intake locations, including plantings, parking areas, garbage disposal bins, and others. | Wildfires & Air Quality Impacts | Landscape | Site | Landscape Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Provide generous outdoor spaces with ample trees and planting to improve local air quality. Consider providing cover in select areas for meetings and meal breaks and to encourage people to use outside spaces. Note the importance of ensuring adequate fuel breaks and/or omitting trees in areas where wildfires are a concern. | Wildfires & Air Quality Impacts | Landscape | Site | Landscape Architect | Neutral | Neutral | Positive | Low |  | Neutral | Neutral
LFV | For planting on site, focus on fire-resistant vegetation with moist, supple leaves and/or low sap production. | Wildfires & Air Quality Impacts | Landscape | Site | Landscape Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Focus on low-pollen trees and plantings to minimize allergens. | Wildfires & Air Quality Impacts | Landscape | Site | Landscape Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Explore whether the building is at high risk of flooding. If high, determine whether below-grade floors should be included into design at all (i.e. survivability test). Dovetail with site selection and site programming. | Flooding | General Resilience | Building | Architect | Neutral | Positive | Neutral | Low |  | Neutral | Neutral
HCDG | Wherever possible, locate key services (e.g. electrical rooms, back-up power) on higher floors at little risk of flooding. Locate electrical room, unit substation, generator and fuel on a floor above future flood construction level. | Flooding | General Resilience | Building | Architect | Neutral | Positive | Neutral | Low |  | Neutral | Neutral
| Install a piezometer on site at least one year prior to construction, to inform base infiltration design. | Flooding | General Resilience | Site | Owner/Operator | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Ensure elevator controls and all major electrical components are placed above the flood construction level to avoid flooded areas and inspect elevators after a flood. | Flooding | Electrical | Building | Electrical | Neutral | Positive | Neutral | Low |  | Neutral | Neutral
HCDG | Ensure hydraulic elevator machine rooms are located above the flood construction level to prevent flooding, and install locking systems (e.g. float switch systems) to prevent elevator cabs from descending below lowest floor or base flood level. | Flooding | Electrical | Building | Electrical | Neutral | Positive | Neutral | Low |  | Neutral | Neutral
HCDG | Separate electrical panels for parkade and for levels above future flood construction level (FCL). Allow for safe shut-off of systems below FCL in case of a flood. | Flooding | Electrical | Building | Electrical | Neutral | Positive | Neutral | Low |  | Neutral | Neutral
HCDG | Protect electrical equipment with waterproof enclosures. | Flooding | Electrical | Building | Electrical | Neutral | Positive | Neutral | Low |  | Neutral | Neutral
Horizon | On lower levels that may be subject to flooding, raise electrical outlets to be higher up the wall. | Flooding | Electrical | Building | Electrical | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Identify any rooftop mechanical systems at risk of flooding. Ensure to fix any roof leaks when adding new rooftop equipment. Ensure all mechanical equipment is placed on pedestals/curbs higher than perimeter scuppers. | Flooding | Envelope & Enclosure | Building | Mechanical | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Reinforce underground walls to withstand the pressures from floodwaters (if feasible), and include removable barriers or flood proof doors or gates at all entrances below the FCL. Note need to 'tank' structures below FCL. | Flooding | Envelope & Enclosure | Building | Structural | Negative | Neutral | Neutral | Low |  | Neutral | Neutral
| Provide multiple vent openings in floors below grade through which floodwater can enter and exit to avoid structural damage due to hydrostatic pressure during flooding. | Flooding | Envelope & Enclosure | Building | Structural | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Include measures to protect below grade exterior foundation walls from moisture ingress. Consider holistic approaches, including the use of continuous fully-reinforced membrane waterproofing system and concrete waterproofing ad-mixture (including construction cold-joint waterproofing and at all mechanical or electrical service penetrations through the below-grade foundation walls). Provide accessibility for future repairs. | Flooding | Envelope & Enclosure | Building | Envelope | Neutral | Positive | Neutral | Low |  | Neutral | Neutral
HCDG | Where necessary, select higher performance, water-resistant building materials to reduce damage to building structure, envelope and interior finishes. Ensure that materials are also mould-resistant. | Flooding | Envelope & Enclosure | Building | Envelope | Neutral | Positive | Neutral | Low |  | Increase | Neutral
HCDG | Provide additional potable water storage or additional water treatment capacity to ensure potability of supply during flood events. Look for locations to store water conveniently (e.g. on the roof coupled with seismic damper) to provide continued access to potable water under conditions where the water supply has been contaminated. | Flooding | Envelope & Enclosure | Building | Plumbing | Neutral | Positive | Neutral | Low |  | Neutral | Neutral
HCDG | Slope lower level towards a dedicated location to allow for pumping of flood water (e.g. parkade vent shaft). Identify potential for use of existing programming (parking) as detention. | Flooding | Plumbing & Storm/Sewer | Building | Structural | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Account for 'short cuts' for floodwaters to and within a building (e.g. shafts, soil gas vents, electrical conduits). Consider performance of area drains in landscaped plazas below future flood construction level. | Flooding | Plumbing & Storm/Sewer | Building | Envelope | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Install heavy-duty duplex sump pumps at the lowest point of the floor, with back-up power supply and regular testing. Using pump controllers, alternate lead and lag pump on a regular basis (e.g. quarterly) to distribute excess wear and lessen chance that pumps will burn-out during a major flood event. | Flooding | Plumbing & Storm/Sewer | Building | Plumbing | Neutral | Neutral | Neutral | Negative |  | Neutral | Increase
HCDG | Install check valves or backflow valves in third pipe, storm and sanitary sewer lines. Install check valves in the body of any below grade floor drains and/or permanently seal any floor drains that are no longer required. Note that backflow valves on sanitary systems must be specified as 'normally open' to allow air flow during normal conditions. Include an alarm and/or warning when valves are closed from flooding to warn occupants against using water in the building. | Flooding | Plumbing & Storm/Sewer | Building | Plumbing | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Install on-site sanitary and storm holding tanks in event the municipal system is compromised. Determine design requirements for sizing the sanitary holding tank. | Flooding | Plumbing & Storm/Sewer | Site | Plumbing | Neutral | Positive | Positive | Low |  | Neutral | Neutral
HCDG | Conduct topological site survey and grading review to better understand stormwater flows. | Flooding | Plumbing & Storm/Sewer | Site | Landscape Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Review maps of historical streams and watercourses, many of which are now piped, to better understand water flow on and near the site. | Flooding | Plumbing & Storm/Sewer | Site | Landscape Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
MBAR | Emphasize natural grade to direct water around and away from buildings. | Flooding | Plumbing & Storm/Sewer | Site | Landscape Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Carry out smoke or dye testing to determine off-site capacity of the storm and sanitary systems. | Flooding | Plumbing & Storm/Sewer | Off-site | Owner/Operator | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Program space in the planning phase for storage of temporary flood barriers close to where they will be used. | Flooding | Operations | Building | Architect | Neutral | Positive | Neutral | Low |  | Neutral | Neutral
EGC | If flooding occurs, engage professional cleaning teams and use commercial equipment to dry out affected areas to prevent mould growth. | Flooding | Operations | Building | Owner/Operator | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Ensure downspouts are directed to rock pits (where geology allows) or detention facilities and away from backfill zones. Ensure rainwater volumes are not directly conveyed to the storm sewer systems, except where stormwater systems are designed to accommodate flows. | Flooding | Landscape | Site | Plumbing | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Install native vegetation and green infrastructure (e.g. rain gardens, infiltration swales, green roofs, rainwater harvesting, daylighted streams and constructed wetlands) to improve water detention, conveyance, and ground permeability. Use flood- and contamination-resistant species where possible. | Flooding | Landscape | Site | Landscape Architect | Positive | Neutral | Neutral | Moderate | Materials Management: - Reduce embodied carbon (through reducing hardscapes). - Increase carbon sequestration (through plantings and vegetation). - Additionally, this strategy contributes to reducing heat island effect. | Decrease | Decrease
HCDG | Incorporate landscape features such bioswales with native plants to absorb and redirect water on-site. Identify surface flow paths from local plans to avoid inadvertently interrupting these paths. | Flooding | Landscape | Site | Landscape Architect | Positive | Neutral | Neutral | Moderate | Materials Management: - Reduce embodied carbon (through reducing hardscapes). - Increase carbon sequestration (through plantings and vegetation). - Additionally, this strategy contributes to reducing heat island effect. | Decrease | Decrease
HCDG | Where appropriate considering site geology, use permeable paving materials and slope grade away from structures to improve overall rainwater infiltration capacity of the site, reducing the pressure on sewer systems. | Flooding | Landscape | Site | Landscape Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Design site stormwater conveyance away from structures for increased volumes and flows. | Flooding | Landscape | Site | Landscape Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
LFV | Include loops in cables for mechanical equipment to take up flex during a seismic event. | Seismic Events | Mechanical | Building | Mechanical | Neutral | Positive | Neutral | Low |  | Neutral | Neutral
LFV | Construct the building out of mass timber, which has been shown to limit damage during a seismic event and facilitate quicker recovery afterwards. | Seismic Events | Architectural | Building | Architect | Positive | Positive | Neutral | High | Materials Management: - Reduce embodied carbon. | Decrease | Neutral
LFV | Utilize performance-based seismic design for the building structure. | Seismic Events | Architectural | Building | Structural | Neutral | Positive | Neutral | Low |  | Neutral | Neutral
MBAR | In large buildings, avoid the use of 'soft stories' that are more vulnerable to collapse. | Seismic Events | Architectural | Building | Structural | Neutral | Positive | Neutral | Low |  | Neutral | Neutral
LFV | Integrate strong motion instrumentation to augment post-earthquake inspection. | Seismic Events | Architectural | Building | Structural | Neutral | Positive | Neutral | Low |  | Neutral | Neutral
HCDG | Provide increased space near generators for more fuel storage. | Power Outage | Electrical | Building | Architect | Negative | Positive | Neutral | Low |  | Neutral | Neutral
HCDG | Provide back-up power to cooling systems at a minimum for priority service areas and priority process loads. | Power Outage | Electrical | Building | Electrical | Neutral | Positive | Neutral | Negative | - Backup power systems are typically fuelled by higher carbon fuels. - Providing cooling from back-up power in addition to other essential services may increase GHG emissions. | Neutral | Increase
HCDG | Provide back-up power for building management control systems. | Power Outage | Electrical | Building | Electrical | Neutral | Positive | Neutral | Negative | - Backup power systems are typically fuelled by higher carbon fuels. - Providing cooling from back-up power in addition to other essential services may increase GHG emissions. | Neutral | Increase
HCDG | Consider potential decrease in solar photovoltaic electricity production during wildfire smoke events. | Power Outage | Electrical | Building | Electrical | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Include structured attachments for solar photovoltaic equipment to account for increased wind loads and to ensure panel will not lift off during extreme events. | Power Outage | Electrical | Building | Electrical | Neutral | Positive | Neutral | Low |  | Neutral | Neutral
HCDG | Incorporate demand management and load sharing for critical loads. | Power Outage | Electrical | Building | Electrical | Positive | Positive | Neutral | Moderate | Energy Efficiency & Emissions Reductions: - Demand management and load sharing reduces spikes and lows therefore making renewable energy options more feasible. | Neutral | Decrease
HCDG | Explore the use of hybrid system for back-up power generators (i.e. not entirely reliant on fuel or solar). Where this is not appropriate, design for more flexible and robust diesel fuel generator systems. | Power Outage | Electrical | Building | Electrical | Positive | Positive | Neutral | Moderate | Energy Efficiency & Emissions Reductions: - Onsite renewable energy and battery storage may reduce operational GHG emissions, particularly if it is able to replace diesel back-up generators. | Neutral | Decrease
HCDG | If not incorporated upfront, provide rough-ins for solar photovoltaic equipment to ensure building is 'solar-ready'. | Power Outage | Electrical | Building | Electrical | Positive | Neutral | Neutral | Moderate | Energy Efficiency & Emissions Reductions: - Onsite renewable energy and battery storage may reduce operational GHG emissions, particularly if it is able to replace diesel back-up generators. | Neutral | Decrease
HCDG | Zone spaces throughout the building as critical and non-critical to minimize required back-up power. | Power Outage | Electrical | Building | Electrical | Positive | Positive | Neutral | Moderate | Energy Efficiency & Emissions Reductions: - All non-critical zones can be left without backup power in a outage. | Neutral | Decrease
HCDG | Review the feasibility of using battery storage. If not feasible, plan to accommodate future use of battery storage and decreased use of fossil fuels. | Power Outage | Electrical | Site | Electrical | Positive | Neutral | Neutral | Moderate | Energy Efficiency & Emissions Reductions: - Incorporating batteries may make onsite renewable energy more feasible, thus lowering operational carbon emissions. - However, batteries also have significant embodied carbon and environmental costs associated with them, so lifecycle assessments should be performed on the systems with and without batteries before incorporating batteries into the building power design. | Increase | Decrease
HCDG | Encourage flexibility in power management through load shedding and time-of-day usage. | Power Outage | Electrical | Site | Owner/Operator | Positive | Positive | Neutral | Moderate | Energy Efficiency & Emissions Reductions: - Demand management and load sharing reduces spikes and lows therefore making renewable energy options more feasible. | Neutral | Decrease
| Design electric vehicle (EV) charging infrastructure on the site to facilitate power sharing (i.e. capable of sharing the energy storage in EV batteries with the building when needed). | Power Outage | Electrical | Site | Owner/Operator | Positive | Neutral | Neutral | Low | Energy Efficiency & Emissions Reductions: - Incorporating batteries may make onsite renewable energy more feasible, thus lowering operational carbon emissions. - However, batteries also have significant embodied carbon and environmental costs associated with them, so lifecycle assessments should be performed on the systems with and without batteries before incorporating batteries into the building power design. | Increase | Decrease
HCDG | Educate operators on what loads are included on back-up power, looking to CSA 282 for what is considered vital, conditional, delayed and normal. | Power Outage | Operations | Building | Electrical | Neutral | Positive | Neutral | Low |  | Neutral | Neutral
MBAR | Maximize natural daylighting in corridors and stairwells to enable vital areas to be usable during a power outage. Include luminescent strips to enhance safety in dark spaces. | Power Outage | Architectural | Building | Structural | Neutral | Positive | Neutral | Moderate | Energy Efficiency & Emissions Reductions: - Optimizing daylighting may reduce daytime energy demands from lighting. | Neutral | Decrease
HCDG | Consider provision of multiple types and sources of back-up power, particularly for buildings with poor envelope performance or more than 6-storeys. | Power Outage | Electrical | Building | Electrical | Positive | Positive | Neutral | Moderate | Energy Efficiency & Emissions Reductions: - Onsite renewable energy and battery storage may reduce operational GHG emissions, particularly if it is able to replace diesel back-up generators. | Neutral | Decrease
HCDG | Avoid rooftop/exterior equipment wherever possible, making use of larger penthouses and/or louvres to protect equipment. | Wind & Storms | Mechanical | Building | Mechanical | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Ensure rooftop equipment and renewable energy systems (e.g. solar PV) are designed to withstand extreme wind or precipitation. | Wind & Storms | Mechanical | Building | Electrical | Neutral | Positive | Neutral | Low |  | Neutral | Neutral
HCDG | Select impact-resistant building materials, external claddings and glazing where continuous load path may be insufficient to protect the structure (e.g. heat soaked glazing). | Wind & Storms | Envelope & Enclosure | Building | Envelope | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Mitigate increased wind load using aerodynamically efficient structures to reduce deflection and resonance, including curved corners, minimized eave overhangs and better foundation design. | Wind & Storms | Architectural | Building | Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Ensure that building attachment details are capable of withstanding stronger winds, focusing on anchorage between different elements (e.g. floors to walls, cladding to building). | Wind & Storms | Architectural | Building | Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Consider wind pressure and wind tunnel effects when selecting the location and design of the main entrance. | Wind & Storms | Architectural | Building | Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Consider topography and landscape details that can help to mitigate high winds. Design the site with wind breaks and buffers to help people can get safely from transit and parking to the building. | Wind & Storms | Landscape | Site | Landscape Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Determine early on whether to retain snow or let it slide off of the roof and design for those intended conditions. | Snowfall | Structural | Building | Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Account for accompanying extreme wind events with snow fall as appropriate. | Snowfall | Structural | Building | Structural | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | For snow sliding off of roof, ensure no roof penetrations or roof feature restrain the snow which could lead excessive loads on these elements. | Snowfall | Envelope & Enclosure | Building | Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Look at ice curl if snow is allowed to slip off of roof to a colder eave section which can push the wall below. | Snowfall | Envelope & Enclosure | Building | Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Look at effects of ponding water above the exterior wall from ice damming . | Snowfall | Envelope & Enclosure | Building | Envelope | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Design roof geometries and appurtenances to consider extreme snowfall events, including the risk of snow dropping from one roof structure to another, which can cause major damage after periods of heavy accumulation. | Snowfall | Architectural | Building | Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Locate mechanical equipment indoors for protection and ease of servicing. | Snowfall | Architectural | Building | Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Consider protection of roof assemblies to allow for increased snow removal and access to equipment. | Snowfall | Architectural | Building | Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Identify appropriate amount of water storage based on projected drought scenarios. | Water Shortage & Drought | Plumbing & Storm/Sewer | Building | Plumbing | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Identify locations for non-potable water storage on site. | Water Shortage & Drought | Plumbing & Storm/Sewer | Site | Plumbing | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Consider rainwater collection systems as a source of non-potable water and passive cooling during water shortages. | Water Shortage & Drought | Plumbing & Storm/Sewer | Site | Plumbing | Neutral | Positive | Neutral | Low |  | Neutral | Neutral
HCDG | Advocate for the use of and/or introduce purple pipe system for wastewater reuse (specifically clean reverse osmosis 'waste' water) that can supplement non-potable uses. | Water Shortage & Drought | Plumbing & Storm/Sewer | Site | Plumbing | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Install outdoor water fixtures capable of operating on water pressure (i.e. without electricity) in a location easily accessible to building occupants and community members. | Water Shortage & Drought | Plumbing & Storm/Sewer | Site | Plumbing | Neutral | Positive | Neutral | Low |  | Neutral | Neutral
HCDG | Make use of drought-tolerant species in landscaping. | Water Shortage & Drought | Landscape | Site | Landscape Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Explore the use of drip irrigation instead of sprinklers. | Water Shortage & Drought | Landscape | Site | Landscape Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Explore the use of collected rainwater for irrigation. | Water Shortage & Drought | Landscape | Site | Landscape Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | Ensure that details and junctions of envelope components allow for adequate drainage and drying. Combine robust air barrier with external insulation, and locate the structure on the interior of the enclosure to reduce thermal bridging and condensation potential. | Moisture & Humidity | Envelope & Enclosure | Building | Envelope | Positive | Neutral | Neutral | Moderate | Materials Management: - Ensuring proper drainage and drying of building materials may extend the life of the materials, thereby reducing embodied GHG emissions associated with the building. | Decrease | Neutral
HCDG | In window and façade design, emphasize the four Ds: deflect, drain, dry and durability. | Moisture & Humidity | Architectural | Building | Architect | Neutral | Neutral | Neutral | Moderate | Materials Management: - Ensuring proper drainage and drying of building materials may extend the life of the materials, thereby reducing embodied GHG emissions associated with the building. | Decrease | Neutral
HCDG | Ensure materials that may be subjected to high humidity conditions or liquid are chosen based on material and assembly performance, as proven by either testing or from prior evidence of success in similar conditions. | Moisture & Humidity | Architectural | Building | Architect | Neutral | Neutral | Neutral | Moderate | Materials Management: - Using materials with higher durability to humidity may extend the lifetime of the material with the building, thereby reducing embodied GHG emissions within the building. | Decrease | Neutral
HCDG | Locate mechanical exhaust away from any roof or wall surfaces or eaves, as escaping warm air can carry moisture that exacerbates freeze/thaw challenges. | Freeze/Thaw | Mechanical | Building | Mechanical | Neutral | Neutral | Neutral | Moderate | Materials Management: Avoiding excess humidity within building materials may extend the life of the materials, thereby reducing embodied GHG emissions associated with the building. | Decrease | Neutral
HCDG | Include small roof overhangs to prevent moisture ingress into building materials, recognizing that large overhangs can increase vulnerability to extreme wind. | Freeze/Thaw | Envelope & Enclosure | Building | Envelope | Neutral | Neutral | Neutral | Moderate | Materials Management: Avoiding excess humidity within building materials may extend the life of the materials, thereby reducing embodied GHG emissions associated with the building. | Decrease | Neutral
RELi | Run water pipes through interior walls and heated spaces to prevent frozen pipes. | Freeze/Thaw | Plumbing & Storm/Sewer | Building | Plumbing | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
RELi | Monitor interior building temperature to prevent freezing of interior piping such as domestic water and fire protection sprinkler systems. | Freeze/Thaw | Plumbing & Storm/Sewer | Building | Plumbing | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
HCDG | In areas that will be subject to increased freeze/thaw, minimize use of permeable, hard building materials (e.g. exposed concrete, brick). | Freeze/Thaw | Architectural | Building | Architect | Neutral | Positive | Neutral | Low |  | Neutral | Neutral
MBAR | Use concrete mixes with reduced water content to minimize risk of structural degradation from changes in freeze-thaw cycles. | Freeze/Thaw | Architectural | Building | Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
MBAR | Design the building to enable direct visual and physical connection to shared social spaces and to nature (e.g. units and balconies framing shared open air courtyards). | Social Dimensions | Social Connection | Building | Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
MBAR | Design movement corridors to encourage sociability by including wide walkways, benches, staircases with room for seating, etc. | Social Dimensions | Social Connection | Building | Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
MBAR | Locate shared spaces (e.g. laundries, gardens, lounges, mail boxes) strategically to promote spontaneous social interaction during the course of the day. | Social Dimensions | Social Connection | Building | Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
MBAR | Locate common facilities such as laundries and bike rooms in areas frequented by day-to-day building users, and design these facilities so passersby can easily see into them. | Social Dimensions | Social Connection | Building | Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
MBAR | Place amenity rooms and lounges across from common facilities (e.g. laundries, mail rooms, etc.) to encourage interactions between neighbours. | Social Dimensions | Social Connection | Building | Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
MBAR | Include community services on the ground floor (e.g. daycare services, community centres). | Social Dimensions | Social Connection | Building | Owner/Operator | Neutral | Positive | Positive | Low |  | Neutral | Neutral
MBAR | Introduce or improve accessible amenity space that residents can use (at no cost) to hold social gatherings. | Social Dimensions | Social Connection | Building | Owner/Operator | Neutral | Positive | Neutral | Low |  | Neutral | Neutral
MBAR | Appoint a space for a community events calendar and for posting notices of interest to residents (e.g. bulletin board in common area). | Social Dimensions | Social Connection | Building | Owner/Operator | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
MBAR | Host recurring social events where new residents can meet and interact with more-established residents of the building. | Social Dimensions | Social Connection | Building | Owner/Operator | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
MBAR | Appoint a social concierge/resident animator to organize common activities such as dog walking, gardening, and child minding. | Social Dimensions | Social Connection | Building | Owner/Operator | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
MBAR | Initiate or support lending libraries, tool share programs, clothing swaps, and other collaborative activities. | Social Dimensions | Social Connection | Building | Owner/Operator | Neutral | Neutral | Negative | Low |  | Neutral | Neutral
MBAR | Establish and/or support opportunities for residents to bond over healthy, local food (e.g. shared kitchens, community gardens, community pantries, long tables). | Social Dimensions | Social Connection | Building | Owner/Operator | Positive | Neutral | Negative | Moderate | Energy Efficiency & Emissions Reductions: - Community food gardens may reduce transportation emissions. | Neutral | Decrease
MBAR | Remove barriers for residents visiting friends throughout the building (e.g. allow residents to access multiple floors). | Social Dimensions | Social Connection | Building | Owner/Operator | Neutral | Neutral | Negative | Low |  | Neutral | Neutral
MBAR | Co-create spaces for healing and spiritual connection that are accessible to residents and community members. | Social Dimensions | Social Connection | Building | Owner/Operator | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
MBAR | Ensure residents have access to natural green spaces and patio areas to reduce stress and provide pleasant outdoor spaces to meet. | Social Dimensions | Social Connection | Site | Landscape Architect | Neutral | Positive | Neutral | Low |  | Neutral | Neutral
MBAR | Design the private realm (e.g. interior courtyards) to allow for public access and encourage permeability between public and private spaces. | Social Dimensions | Social Connection | Site | Landscape Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
MBAR | Design landscaping to accommodate building- or community-scale gardens and promote a connection to nature. | Social Dimensions | Social Connection | Site | Landscape Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
MBAR | Include playgrounds and other child-oriented infrastructure into landscape design. | Social Dimensions | Social Connection | Site | Landscape Architect | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
MBAR | Whenever possible, site buildings in family-oriented neighbourhoods near schools and community services. | Social Dimensions | Social Connection | Site | Owner/Operator | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
MBAR | Support building-scale emergency messaging via SMS and/or computer/television interruptions as way to share emergency notifications. | Social Dimensions | Resident Preparedness | Building | Owner/Operator | Neutral | Positive | Positive | Low |  | Neutral | Neutral
MBAR | Support weather event alert systems that indicate when there is an emergency in the community. | Social Dimensions | Resident Preparedness | Building | Owner/Operator | Neutral | Neutral | Neutral | Low |  | Neutral | Neutral
MBAR | Arrange assistance for people with special needs to organize their emergency supplies (medications, instructions for caregivers, etc.) | Social Dimensions | Resident Preparedness | Building | Owner/Operator | Neutral | Positive | Positive | Low |  | Neutral | Neutral
MBAR | Promote and/or support collective emergency planning amongst neighbours, as opposed to as individual households, which can support bulk purchases and shared resources. | Social Dimensions | Resident Preparedness | Building | Owner/Operator | Neutral | Positive | Positive | Low |  | Neutral | Neutral
MBAR | Build collective resilience and enhance capacity to respond through emergency preparedness workshops. | Social Dimensions | Resident Preparedness | Building | Owner/Operator | Neutral | Positive | Positive | Low |  | Neutral | Neutral
MBAR | Provide applicable building personnel and interested residents with basic emergency response training (e.g. first aid, fire suppression). Designate building or community members with first aid or other experience as emergency coordinators. | Social Dimensions | Resident Preparedness | Building | Owner/Operator | Neutral | Positive | Positive | Low |  | Neutral | Neutral
MBAR | Develop a buddy system where neighbours agree to check in on each other in the event of an emergency. Provide indicators for those who need assistance to place on their door or window, with multiple neighbours agreeing to look our for the safety of these individuals in case of emergency. | Social Dimensions | Resident Preparedness | Building | Owner/Operator | Neutral | Positive | Positive | Low |  | Neutral | Neutral
MBAR | Ensure that building personnel are aware of residents that may need extra assistance during an emergency, including seniors and those with mobility challenges. | Social Dimensions | Resident Preparedness | Building | Owner/Operator | Neutral | Positive | Positive | Low |  | Neutral | Neutral
MBAR | Provide a resilient potable water supply to allow for universally accessible drinking water (e.g. gravity-fed rooftop water tanks). | Social Dimensions | Resident Preparedness | Site | Owner/Operator | Neutral | Positive | Neutral | Low |  | Neutral | Neutral
MBAR | Mobilize knowledge and build evolutionary learning networks by collaborating with other multifamily housing developers and providers to make resilience plans stronger and more effective. | Social Dimensions | Resident Preparedness | Off-site | Owner/Operator | Neutral | Positive | Positive | Low |  | Neutral | Neutral
MBAR | Share experiences in resilience planning and emergency preparedness with other organizations, perhaps collaborating with existing events (e.g. business association meetings). | Social Dimensions | Resident Preparedness | Off-site | Owner/Operator | Neutral | Positive | Positive | Low |  | Neutral | Neutral
© BC Housing 2022
Climate-ready Housing Design Guide V1

## Reference - CSA Standards
Standard | Description | Reference
CSA A123.24:21 Standard test method for wind resistance of modular vegetated roof assembly | Provides requirements for wind resistance testing of vegetated roof assemblies. The requirements specified include specimen set-up, instrumentation and apparatus, testing procedures, and termination. | https://www.csagroup.org/store/product/CSA%20A123.24%3A21/
CSA A123.26:21 Performance requirements for climate resilience of low slope membrane roofing systems | Outlines requirements for low slope membrane roofing systems (LSMRS) when identified as silver and gold performance level based on the climate severity and resilience requirements. | https://www.csagroup.org/store/product/CSA%20A123.26%3A21/
CSA A440.2-19/A440.3-19 Fenestration energy performance/User guide to CSA A440.2:19, Fenestration energy performance | Applies to the determination of energy performance properties for a variety of fenestration systems, including fixed windows, operable windows, sliding glass doors, hinged doors, skylights with flat glazings, and curtain walls. Annex B provides some information on how climate change can affect fenestration product design and application | https://www.csagroup.org/store/product/2702116/
CSA SPE-112:21 CarbonStarⓇ: Technical specification for concrete carbon intensity quantification and verification | Provides minimum requirements and recommendations for the quantification and verification of the carbon intensity in a unit of concrete, including any carbon that is permanently sequestered during the production of the concrete and/or its input materials. Therefore, this number could be either positive or negative | https://www.csagroup.org/store/product/CSA%20SPE-112%3A21/
CSA Z240.10.1-19 Site Preparation, Foundation, and Installation of Buildings | Applies to single- and multi-section buildings supported on longitudinal floor beams, or perimeter rim joists designed to perform as beam. 2019 edition contains guidance on calculation and climate change data | https://www.csagroup.org/store/product/2700095/
CSA Z800-18 Guideline on Basement Flood Protection and Risk Reduction | Covers measures to reduce the risks of basement flooding, and to mitigate the adverse effects on property, public safety, and public health in case of a flood event. It covers existing, new, rebuilt, and renovated houses in rural and urban settings. | https://www.csagroup.org/store/product/Z800-18/
Climate Change Adaptation of Masonry Materials, Design, and Construction | This report provides recommendations for the adaptation of masonry standards to the effects of climate change. Included is a detailed review of the literature related to the effects of climate and climate change on masonry materials and design, as well as a discussion of how this information may be used to strengthen current standards | https://www.csagroup.org/article/research/climate-change-adaptation-of-masonry-materials-design-and-construction/
Climate Change Adaptation and the Canadian Electrical Code Series |  | https://community.csagroup.org/docs/DOC-124897
DC Microgrids in Buildings – Planning Today for Tomorrow’s Needs | CSA Group published a research report in March 2019 [1], which produced an important knowledge base, as well as a list of high-priority items for standards development. To expand upon the initial research, this report summarizes insights from a workshop involving over 40 Canadian industry stakeholders who were asked to visualize the DC microgrids of the future (2030); explore the DC microgrid value; uncover tools needed to capture that value; and identify solutions to barriers and opportunities. | https://www.csagroup.org/article/research/dc-microgrids-in-buildings-planning-today-for-tomorrows-needs/
Energy Management of Building Power Distribution | This research project developed a model for dynamically reconfiguring the electrical distribution grid within commercial buildings and dynamically dispatching power to commercial building loads | https://www.csagroup.org/article/research/energy-management-building-power-distribution-systems/
CSA W200-18 Design of Bioretention Systems | Provides requirements and recommendations for the design of bioretention systems intended for the management of urban stormwater runoff | https://www.csagroup.org/store/product/W200-18/
CSA W201-18 Construction of Bioretention Systems | Covers roles and responsibilities; contract documentation; construction sequencing; erosion and sediment control for bioretention systems; construction documentation; material supply and handling; installation considerations; landscape materials and maintenance; construction warranty maintenance; and assumption protocols | https://www.csagroup.org/store/product/W201-18/
CAN/CSA W202-18 Erosion and sediment control inspection and monitoring | Provides requirements for the inspection and monitoring of erosion and sediment control measures installed on construction sites | https://www.csagroup.org/store/product/CAN%25100CSA-W202-18/
CSA W204-19 Flood Resilient Design for New Residential Communities | Provides compliance criteria and guidance on the design of flood- resilient new residential communities as it relates to greenfield development only | https://www.csagroup.org/store/product/CSA%20W204%3A19/
CSA W210:21, Prioritizing flood resiliency in existing residential communities | Provides voluntary guidance on a flood hazard and vulnerability screening framework | https://www.csagroup.org/store/product/CSA%20W210%3A21/
CSA W211:21 Management standard for stormwater systems | Provides requirements and recommendations for management of stormwater systems. It defines a risk-based process for decision makers responsible for the operation, maintenance, and management of stormwater systems | https://www.csagroup.org/store/product/CSA%20W211%3A21/
F280-12 (R2021), Determining the required capacity of residential space heating and cooling appliances |  | https://www.csagroup.org/store/product/F280-12/
© BC Housing 2022
Climate-ready Housing Design Guide V1
RELEVANT EXISTING CSA STANDARDS (2022)
The following CSA standards are provided for reference to compare current practice against recommendations in this Guide for more climate resilient design standards.